## Below 200k
REG_ID | Reg Name | Time | Areas | Planning Methodology | Proposed time in 2022 DTAPR | Reason for change
DOC_11.03.38 | Optical Arc Fault Protection | 2024,2025,2026,2027,2028, | Homebush,Oatley,Ourimbah,Sydney CBD,Sydney Northeast,Sydney Northwest, | The optical arc fault protection program is driven by the need to protect the safety of workers so far as is reasonably practicable at substations. The present summated current protection schemes are inadequate and will be replaced with the modern standard optical arc fault protection systems. The modern optical arc fault protection systems will also operate to limit the damage to other network assets. | 2023,2024,2025,2026,2027, | no change
DOC_11.03.54 | Asbestos Fire Doors - ZN & TS | 2024,2025,2026,2027,2028, | Newcastle ,Sydney CBD, | The primary function of a fire door is to prevent the spread of fire. Asbestos contained within these fire doors is a safety risk to workers and the public. Ausgrid has a duty of care to eliminate or where this is not practicable minimise safety risks to as low as is reasonably practicable. | 2023,2024,2025,2026,2027, | no change
DOC_11.03.69 | Siemens 8DN8 Circuitry Modification - ZN | 2024,2025,2026,2027,2028, | Homebush,Newcastle ,Ourimbah,Sydney CBD,Sydney Northeast, | The Siemens 8DN8 low gas alarm circuitry renewal is driven by the National Electricity Rules compliance that prevents a single point of failure that would cause both primary and backup protection to fail. The present configuration does not meet this requirement as the failure of the low gas alarm sensor can inhibit the operation of the primary and back-up protection systems. Renewal of the circuitry will eliminate this failure mode. | 2023,2024,2025,2026,2027, | no change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 2024,2025,2026,2027,2028, | Homebush,Lower Hunter ,Newcastle ,Oatley,Ourimbah,Sydney CBD,Sydney Northeast,Sydney Northwest | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024,2025,2026,2027, | no change
DOC_11.03.77 | Substation Locks Upgrade | 2025,2026, | Homebush,Lower Hunter ,Newcastle ,Oatley,Ourimbah,Sydney CBD,Sydney Northeast,Sydney Northwest,Upper Hunter | Ausgrid has a duty of care to the public and its workers by limiting access to hazardous electrical equipment. Substations contain hazardous electrical equipment that has the potential to harm the public. Unauthorised access with the intent to harm and disrupt is also considered as a possibility. This program will improve the security of Ausgrid's substations. | 2023,2024, | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.02 | A,B & C Type Kiosks | 2024,2025,2026,2027,2028, | Homebush,Sydney CBD,Sydney Northeast,Sydney Northwest, | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment. | 2023,2024,2025,2026,2027, | no change
REP_01.02.42 | Outdoor Enclosure Substations | 2024,2025,2026,2027,2028, | Homebush,Oatley,Sydney CBD,Sydney Northeast,Sydney Northwest, | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations. | 2023,2024,2025,2026,2027, | no change
REP_01.02.43 | HV OCB Subs | 2024,2025,2026,2027,2028, | Homebush,Newcastle ,Oatley,Sydney CBD,Sydney Northeast,Sydney Northwest, | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk. | 2023,2024,2025,2026,2027, | no change
REP_01.02.45 | Statter_ALM_Godfrey HV Fuse Switches | 2024,2025,2026,2027,2028, | Homebush,Oatley,Ourimbah,Sydney CBD,Sydney Northeast,Sydney Northwest, | These HV fuse switches are being replaced due to increasing number of failures and limited availability of spares as well as technical support being no longer available. Majority of the switches are oil filled and failures can pose serious public safety risks if a fire follows the failure. | 2023,2024,2025,2026,2027, | no change
REP_01.02.47 | Reyrolle JKSS RMIs C_EB | 2024,2025,2026, | Homebush,Sydney CBD, | The Reyrolle JKSS RMIs have a range of safety and operational issues and they are approach their end of life. These assets are experiencing a range of asset condition issues including oil leaks from the main tank and corrosion of support structure and main body. Projects within this program are identified based on an asset condition risk assessment. | 2023,2025,2026,2027, | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.52 | Obsolete RMIs & FSs | 2024,2025,2026,2027,2028, | Homebush,Lower Hunter ,Newcastle ,Oatley,Ourimbah,Sydney CBD,Sydney Northeast,Sydney Northwest | This program funds the replacement of 11kV Ring Main Isolators (RMIs) & Fuse Switches (FS) that have been approach their end of life. Projects within this program are identified based on an asset condition risk assessment.. | 2023,2024,2025,2026,2027, | no change
REP_01.02.57 | ABB 11kV Series V EDO Fuse Carriers | 2024,2025, | Homebush,Lower Hunter ,Newcastle ,Ourimbah,Sydney CBD,Sydney Northeast,Sydney Northwest,Upper Hunter | There have been a number of failures associated with ABB Series V 11kV EDO Fuse Carriers used on Pole Top transformer (PT) substations, resulting in customer interruptions and leading to safety and operational concerns for Ausgrid staff and the public. The program is driven by inherent design issues with the construction rather than condition or age. | 2024,2025, | no change
REP_01.02.59 | SCADA Equipment - DC | 2025,2026,2027,2028, | Sydney CBD, | The SCADA equipment in Sydney CBD distribution centres were installed in early 1990s is now approaching end of life and is increasingly difficult to maintain. | 2023,2024,2025,2026,2027, | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.60 | Modems - DC | 2024, | Homebush,Lower Hunter ,Newcastle ,Oatley,Ourimbah,Sydney CBD,Sydney Northeast,Sydney Northwest | Ausgrid's network assets such as auto-reclosers and distribution substations that are controlled/monitored remotely use 3G modems for communications. Ausgrid has been advised by Telstra that the 3G network will be progressively retired starting from 2020. The existing population of modems will not function after the 3G cellular network is decommissioned by Telstra and there is a need to replace them with a modern equivalent. | 2023,2024, | no change
REP_01.03.04 | Single Circuit Breaker Switchgear | 2024,2025,2026,2027,2028, | Homebush,Sydney CBD, | The current population of breakers at single circuit breaker substations are deteriorating. Most of them were commissioned during the 1960s and there are ongoing issues associated with these breakers including oil leaks and difficulties with the operating mechanism. These breakers also utilise copper pilot cables for disconnecting faults and these cables have high failure rates as they are of a similar age to the substation equipment. Locating and repairing defects on these underground communications cables is expensive due to the need to excavate roads to access the cable for repair. Ausgrid has conducted a detailed condition risk assessment of these assets and developed a prioritised planned replacement program to mitigate the risk associated with these assets. | 2023,2024,2025,2026,2027, | no change
REP_01.03.16 | Muswellbrook Kiosks | 2024,2025,2026,2027,2028, | Upper Hunter , | These kiosk substations are approaching their end of life and require replacement. There are a range of asset condition, operational and safety issues associated with this type of substation. Additionally, certain replacement parts for this type of substation are unable to be procured. Projects within this program are identified based on an asset condition risk assessment... | 2023,2024,2025,2026,2027, | no change
REP_01.03.17 | Hazemeyer RMIs - Harsh Environment | 2024,2025,2026,2027,2028, | Homebush,Lower Hunter ,Newcastle ,Oatley,Sydney CBD,Sydney Northeast,Upper Hunter , | The replacement program for Hazemeyer ring main units in harsh environments was initiated following a review of condition of this class of asset. Environmental factors, such as high pollution and salt spray in coastal areas, have affected the condition of these assets. Projects within this program are identified and prioritised based on an asset condition risk assessment. | 2023,2024,2025,2026,2027, | no change
REP_02.02.05 | 33kV Bulk Oil OD Circuit Breakers - ZN & | 2024,2025, | Newcastle , | The 33kV bulk oil, dead tank circuit breakers are experiencing recurring failure modes and pose a high safety risk. In addition, many of these assets are in poor condition. The major risk associated with these assets is due to the bushings failing particularly in outdoor yards as it poses a serious risk to employee and public safety as well as potentially causing secondary damage to other network assets within the substation. Projects within this program are identified and prioritised based on an asset condition risk assessment. | 2023,2024,2025, | no change
REP_02.02.09 | Earthing system - ZN | 2024,2025,2026,2027, | Lower Hunter ,Newcastle ,Oatley,Ourimbah,Sydney CBD,Sydney Northeast,Sydney Northwest,Upper Hunter , | The major substation earthing system is to protect people and the asset as well as endsuring exposed equipment is safe to touch during normal operation. This program funds the replacement of earthing equipment within zone substations and subtransmission substations.
REP_02.02.35 | 33KV Essantee I&Es - ZN & TS | 2024, | Newcastle , | The 33kV Essantee isolator switches have a history of failures which have impacted reliability of the network and the safety of workers. Failure modes include: • Welded primary contacts, or overheating primary contacts; • Corrosion of support steel work; • Security/integrity of earth bar connections and crimps; • Damaged support insulators. In 2007, following a series of failures, an investigation to assess the risks posed by 33kV Essantee isolator switches recommended that all outdoor 33kV Essantee isolator switches be replaced according to a recommended priority list.
REP_02.02.38 | 33KV I&Es - ZN & TS | 2024,2025,2026,2027,2028, | Homebush,Oatley,Ourimbah,Sydney Northeast,Sydney Northwest,Upper Hunter , | The 33kV Non-Essantee isolator switches have a history of failures which have impacted reliability of the network and the safety of workers. Failure modes include: .• Welded primary contacts, or overheating primary contacts;.• Corrosion of support steel work;.• Security/integrity of earth bar connections and crimps;.• Damaged support insulators..Such failures have potential to cause safety and operation issues. Projects within this program are identified and prioritised based on an asset condition risk assessment.. | 2023,2024,2025,2026,2027, | no change
REP_02.02.60 | 11kV Switchboard Protection - ZN & TS | 2024,2025,2026, | Homebush,Lower Hunter ,Sydney CBD,Sydney Northeast, | A significant portion of Ausgrid's 11kV Switchgear protection scheme relays utilise electromechanical technology. These assets have hidden failure modes which mean that failures are not detected until it is required to operate. Many of these older relays are no longer supported by manufacturers and spare parts are not available and replacement involves new technology which takes additional time to install. The program funds the replacement of 11kV busbar protection schemes at end-of-life which extends the effective life of the switchboard. | 2023,2024,2025,2026, | no change
REP_02.02.61 | High Impedance Busbar Protection - ZN & T | 2024,2025, | Newcastle ,Oatley,Sydney Northwest, | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Projects within this program are identified and prioritised based on an asset condition risk assessment. | 2023,2024,2025, | no change
REP_02.02.62 | SCADA Equipment - ZN & TS | 2024,2025,2026,2027,2028, | Newcastle ,Oatley,Ourimbah,Sydney CBD,Sydney Northeast,Sydney Northwest,Upper Hunter , | The SCADA equipment in Sydney CBD zone substations have conditional and aging issues. Considering the high reliability requirement in the CBD area, they are recommended to be replaced. | 2023,2024,2025,2026,2027, | no change
REP_02.03.05 | 132/66kV Bushings - ZN & TS | 2024,2025,2026, | Homebush,Lower Hunter ,Sydney CBD,Sydney Northwest,Upper Hunter , | Oil Impregnated Paper transformer bushings poses risk of explosive failure, which represent a safety hazard and can cause excessive damage to substation equipment. Following the catastrophic failure of several oil impregnated paper bushings on Ausgrid’s network, investigations were carried out into the condition of these assets. The investigations found that there was a degradation of the insulation material resulting in water ingress in the bushing. The seriousness of bushing failures instigated a proactive replacement program of this type of oil impregnated paper bushings. The bushing replacement programs form part of Ausgrid’s strategy to meet its obligations to manage the risks of these assets failing so far as is reasonably practicable. | 2023,2024,2025,2026, | no change
REP_02.03.07 | Protection Relays - ZN & TS | 2024,2025,2026,2027, | Lower Hunter ,Newcastle ,Ourimbah,Sydney CBD,Sydney Northeast,Sydney Northwest, | This program is to replace the protection relays that are in poor condition. Failure of protection relays put primary assets at risk and can lead to safety incidnts, property damage and loss of supply. Projects are identified using a condition assessment process. | 2023,2024,2025,2026,2027, | no change
REP_02.03.08 | High Priority Relays - ZN & TS | 2025,2026, | Newcastle ,Ourimbah,Sydney CBD, | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, these relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. | 2023,2024,2025, | Work has been reprioritised based on condition and risk assessment and available resources.
REP_02.03.10 | Voltage Regulation Equipment - ZN & TS | 2024,2025, | Homebush,Oatley,Sydney CBD,Sydney Northwest, | Failures on voltage regulation groups can cause network voltage levels to drift outside of the permissible network standard range, which can cause damage to customer appliances. Failure of VRs can also lead to the excess operation of primary plant which reduces the life of the asset. Projects within this program are identified and prioritised based on an asset condition risk assessment. | 2023,2024,2025, | no change
REP_02.03.11 | Batteries and Battery Charging Equipment | 2024,2025,2026,2027,2028, | Homebush,Lower Hunter ,Newcastle ,Oatley,Ourimbah,Sydney CBD,Sydney Northeast,Upper Hunter , | Failure of the battery scheme whilst the substation is energised can result in the loss of power to the substation’s electrical protection systems. The dominant failure mode of batteries is the loss of capacity due to an internal fault of the cell, which is a nonrepairable failure mode and requires replacement to ensure the battery meets substation performance requirements. ..Batteries that have degraded are unable to hold charge and will not operate when required. The degradation of battery systems means that they need to be replaced to provide the required function. Battery chargers are matched to the battery technology and therefore need to be replaced upon battery technology change to maintain compatibility | 2023,2024,2025,2026,2027, | no change
REP_04.02.01 | Steel Mains (km) | 2025,2026,2027, | Lower Hunter ,Sydney Northeast,Upper Hunter , | Protective galvanised coating of the steel mains and conductor ties degrades with age and can pose environmental risks, such as fires, public safety and failure of supply. Replacement of the steel mains are identified using an condition assessment process that used inspection, spatial risk factors and failure data. | 2023,2024,2025,2026, | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 2024,2025,2026,2027,2028, | Homebush,Lower Hunter ,Newcastle ,Oatley,Sydney CBD,Sydney Northeast,Sydney Northwest, | Ausgrid has approximately 785km of Low Voltage underground metallic sheathed cable which supply electricity from distribution substations to customers. LV metallic sheathed cable failures can result in consequences including safety risks, fire risk, unserved energy and other risks. A planned replacement strategy has been adopted for the replacement of LV metallic sheathed cable based on a detailed risk assessment. | 2023,2024,2025,2026,2027, | no change
REP_04.02.06 | Low Voltage HDPE Cables (km) | 2024,2025,2026,2027,2028, | Homebush,Oatley,Sydney CBD,Sydney Northeast,Sydney Northwest, | Ausgrid has approximately 110km of LV HDPE cable installed on its distribution network, which was installed between the mid 1970s until the mid 1980s. Ausgrid's HDPE LV cables have higher failure rates than other types of LV cable on the network. ..The need to replace HDPE cables has been triggered by condition related issues which have resulted in;.• safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and.• network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. ..Ausgrid has developed a prioritised planned replacement program of all HDPE cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2023,2024,2025,2026,2027, | no change
REP_04.02.11 | 11kV UGOHs | 2024,2025,2026,2027,2028, | Lower Hunter ,Newcastle ,Oatley,Ourimbah,Sydney Northeast, | Unlike modern UGOHs which use heat shrink insulation, pot head UGOHs can fail explosively as the cables are terminated inside an oil/compound filled metal casing. The failure of pot head UGOHs is exacerbated by being located in outdoor public areas. Potential hazards include injury to public and staff, live conductors falling to the ground. | 2023,2024,2025,2026,2027, | no change
REP_04.02.12 | LV Metallic Sheathed Cables (km) | 2024,2025,2026, | Sydney CBD, | Low voltage metallic sheathed cable failures can result in consequences such as safety risks, fire risks, unserved energy and other risks. A planned replacement strategy is adopted for the replacement of LV metallic sheathed cable based on a detailed risk assessment of Ausgrid's metallic sheathed cable population. | 2023,2024,2025,2026, | no change
REP_04.02.32 | 11kV Essantee ABS HS641 (No.) | 2024, | Oatley,Sydney Northeast,Sydney Northwest, | Air break switches are installed at the top of poles located in public areas. Ausgrid workers stand directly below the air break switches when network switching is undertaken. The need to replace these air break switches has been triggered by a combination of condition and design related issues which have resulted in safety risks to the public, customers and workers due to uncontrolled discharge of electricity or falling components, as well as network reliability risks associated with these failures. Ausgrid workers have experienced ‘near miss’ safety incidents due to failed porcelain insulators falling during network switching and have received electric shocks from poles due to the uncontrolled discharge of electricity from cracked insulators. A functionally failed air break switch is one that has degraded to the point that it is no longer able to be safely operated or has caused a network interruption due to component failure.
REP_04.02.36 | 11kV Taplin ABS D571 (No.) | 2024,2025,2026,2027,2028, | Lower Hunter ,Oatley,Ourimbah,Sydney Northeast,Sydney Northwest, | Air break switches are installed at the top of poles located in public areas. Ausgrid workers stand directly below the air break switches when network switching is undertaken. The need to replace these air break switches has been triggered by a combination of condition and design related issues which have resulted in safety risks to the public, customers and workers due to uncontrolled discharge of electricity or falling components, as well as network reliability risks associated with these failures. Ausgrid workers have experienced ‘near miss’ safety incidents due to failed porcelain insulators falling during network switching and have received electric shocks from poles due to the uncontrolled discharge of electricity from cracked insulators. A functionally failed air break switch is one that has degraded to the point that it is no longer able to be safely operated or has caused a network interruption due to component failure. | 2023,2024,2025,2026,2027, | no change
REP_04.02.43 | 11kV ABS Haycolec (No.) | 2024,2025,2026, | Homebush,Newcastle ,Sydney CBD,Sydney Northeast,Sydney Northwest, | Air break switches are installed at the top of poles located in public areas. Ausgrid workers stand directly below the air break switches when network switching is undertaken. The need to replace these air break switches has been triggered by a combination of condition and design related issues which have resulted in safety risks to the public, customers and workers due to uncontrolled discharge of electricity or falling components, as well as network reliability risks associated with these failures. Ausgrid workers have experienced ‘near miss’ safety incidents due to failed porcelain insulators falling during network switching and have received electric shocks from poles due to the uncontrolled discharge of electricity from cracked insulators. A functionally failed air break switch is one that has degraded to the point that it is no longer able to be safely operated or has caused a network interruption due to component failure. | 2023,2024, | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.46 | HV OH Mains (ACSR/Quince) (km) | 2024,2025,2026,2027,2028, | Homebush,Lower Hunter ,Newcastle ,Oatley,Ourimbah,Sydney CBD,Sydney Northeast,Sydney Northwest,Upper Hunter | The protective galvaniing coating of the steel strands in ACSR conductor and conductor ties degrades due to age and environmental factors. This can result in asset failures and pose riks of network fires, public safety and failure of supply. Assets to be replaced are identified using an asset condition assessment process thast used inspection, spatial risk factors and failure data. | 2023,2024,2025,2026,2027, | no change
REP_04.02.48 | Modems - DM | 2024, | Homebush,Lower Hunter ,Newcastle ,Oatley,Ourimbah,Sydney CBD,Sydney Northeast,Sydney Northwest | Ausgrid's network assets such as auto-reclosers and distribution substations that are controlled/monitored remotely use 3G modems for communications. Ausgrid has been advised by Telstra that the 3G mobile network will be progressively retired starting from 2020. The existing population of modems will not function after the 3G cellular network is decommissioned by Telstra and there is a need to be replaced with a modern equivalent. | 2023,2024, | no change
REP_04.04.01 | LV Overhead Mains - Reactive (km) | 2025,2026, | Homebush,Newcastle ,Oatley,Ourimbah,Sydney CBD,Sydney Northeast,Sydney Northwest, | Degradation of overhead conductors and conductor ties can result in fallen conductors which pose risks to public safety and loss of network supply. This program funds the replacement of conditionally failed LV overhead conductor. It is to replace the overhead conductor including the replacements of all conductor phases in any conductor bay or strain section. The scope also includes sections of dedicated LV circuits of bare or PVC insulated construction that must be replaced when dthey are not able to be removed through transferral to LV mains.
REP_05.02.03 | Refurbish Earthing - TM OH Feeders | 2024,2025,2026,2027,2028, | Homebush,Newcastle ,Ourimbah,Sydney CBD,Sydney Northeast,Sydney Northwest, | Earthing system on subtransmission feeders is critical for ensuring public and workplace safety, protecting assets and ensuring correct system operation. Deteriorated earthing system will lead to increased electric shock risk as well as equipment failure and increased outages. Ausgrid utilises condition information from inspections / earth resistance testing and condition assessments to determine when an earthing system is approaching functional failure and sets criteria aligned to industry standards to define the point of conditional failure. Earthing systems are replaced or refurbished if the condition issues identified are not technically or economically able to repaired i.e. if they are at end of life. | 2023,2024,2025,2026,2027, | no change
REP_05.02.12 | Cable Pressure Alarm Replacement | 2024, | Homebush,Sydney CBD,Sydney Northwest, | Cable pressure alarm systems at the end of their serviceable life pose risks such as environmental damage, delay in response time to implement cable repair, increase in breakdown failures. Projects are prioritised based on asset age, likelihood of failure, condition and expected replacement date of the feeder. | 2023,2024,2025, | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.26 | Ground Stays | 2024, | Newcastle , | The replacement of the ground anchors on sub-transmission overhead lines is in response to the number of failures seen in one particular design of ground anchor, primarily used in the upper and lower Hunter and Newcastle regions. Planned projects are identified using a condition assessment process. | 2023,2024,2025,2026, | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.28 | Replace ST Feeder Earth Electrodes | 2024, | Lower Hunter ,Newcastle , | Ausgrid has a number of transmission feeder lines where the earthing electrodes on each pole has been found to have experienced corrective failures and in some cases are missing (e.g. from theft). This is particularly dangerous as injury/fatality can result without any visual warning signs of a fault. Planned projects have been identified by inspection of the feeder earthing systems. | 2023, | Work has been reprioritised based on condition and risk assessment and available resources.

## Above 200k
REG_ID | Asset Description | Notif # | Notif Desc | Year of Work | Area of work | Planning methodology | Proposed time in 2022 DTAPR | Reason for change
REP_01.02.61 | Intertripping Schemes - DC | 1700438727 | Intertripping Schemes - DC | 2024 | SURRY HILLS | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life.
REP_01.02.61 | Intertripping Schemes - DC | 1700438699 | Intertripping Schemes - DC | 2024 | DARLINGHURST | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.61 | Intertripping Schemes - DC | 1700438749 | Intertripping Schemes - DC | 2024 | GORDON | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life.
REP_01.02.61 | Intertripping Schemes - DC | 1700438723 | Intertripping Schemes - DC | 2024 | ARTARMON | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life.
REP_01.02.61 | Intertripping Schemes - DC | 1700438755 | Intertripping Schemes - DC | 2024 | MALABAR | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life.
REP_01.02.61 | Intertripping Schemes - DC | 1700438692 | Intertripping Schemes - DC | 2024 | REDFERN | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2024 | No Change
REP_01.03.06 | Network Protectors (West CM2/22) | 1700437950 | Network Protectors | 2024 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354243 | DOC LV RECONFIG SLCP481 POLE LE19373 | 2024 | NEWTOWN | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354261 | DOC LV RECONFIG SLCP800 POLE PY53235 | 2024 | KILLARA | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354277 | DOC LV RECONFIG SLCP798 POLE PY55458 | 2024 | GORDON | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354280 | DOC LV RECONFIG SLCP1063 POLE MC07503 | 2024 | NORTH WAHROONGA | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354312 | DOC LV RECONFIG SLCP1388 POLE PY72788 | 2024 | LINDFIELD | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354340 | DOC LV RECONFIG SLCP692 POLE PY58449 | 2024 | EAST KILLARA | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354356 | DOC LV RECONFIG SLCP175 POLE PY43530 | 2024 | PYMBLE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354359 | DOC LV RECONFIG SLCP671 POLE SY16442 | 2024 | RANDWICK | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354362 | DOC LV RECONFIG SLCP1301 POLE PY34633 | 2024 | KILLARA | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354376 | DOC LV RECONFIG SLCP1052 POLE PY55787 | 2024 | LINDFIELD | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354379 | DOC LV RECONFIG SLCP666 POLE MA09793 | 2024 | KINGSFORD | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354380 | DOC LV RECONFIG SLCP907 POLE PY55371 | 2024 | EAST LINDFIELD | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354403 | DOC LV RECONFIG SLCP71 POLE PE05217 | 2024 | ROSELANDS | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354419 | DOC LV RECONFIG SLCP214 POLE MO30224 | 2024 | CREMORNE POINT | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354422 | DOC LV RECONFIG SLCP213 POLE MO33187 | 2024 | NEUTRAL BAY | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354429 | DOC LV RECONFIG SLCP577 POLE LE03291 | 2024 | DULWICH HILL | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354431 | DOC LV RECONFIG SLCP150 POLE PY85082 | 2024 | WEST PYMBLE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354440 | DOC LV RECONFIG SLCP661 POLE MA00347 | 2024 | LITTLE BAY | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354471 | DOC LV RECONFIG SLCP707 POLE MA12174 | 2024 | RANDWICK | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354477 | DOC LV RECONFIG SLCP174 POLE PY63175 | 2024 | PYMBLE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354499 | DOC LV RECONFIG SLCP572 POLE FF71197 | 2024 | ROSEVILLE CHASE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354536 | DOC LV RECONFIG SLCP223 POLE MO29355 | 2024 | MOSMAN | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354570 | DOC LV RECONFIG SLCP667 POLE MA05323 | 2024 | MAROUBRA | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354607 | DOC LV RECONFIG SLCP422 POLE MA07253 | 2024 | MATRAVILLE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354616 | DOC LV RECONFIG SLCP3329 POLE KO17145 | 2024 | CARLTON | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354619 | DOC LV RECONFIG SLCP371 POLE MA04778 | 2024 | MAROUBRA | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354642 | DOC LV RECONFIG SLCP1741 POLE MA07936 | 2024 | MAROUBRA | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354693 | DOC LV RECONFIG SLCP882 POLE MA05431. | 2024 | MAROUBRA | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354752 | DOC LV RECONFIG SLCP53 POLE LE14516 | 2024 | PETERSHAM | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354755 | DOC LV RECONFIG SLCP224 POLE MO26936 | 2024 | MOSMAN | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354819 | DOC LV RECONFIG SLCP1238 POLE BE84753 | 2024 | BEROWRA | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354960 | DOC LV RECONFIG SLCP1303 POLE PY42383 | 2024 | PYMBLE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354966 | DOC LV RECONFIG SLCP763 POLE MA06782 | 2024 | KINGSFORD | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700355140 | DOC LV RECONFIG SLCP7240 POLE BV00868 | 2024 | CHITTAWAY BAY | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700355181 | DOC LV RECONFIG SLCP165 POLE PY16852 | 2024 | WAHROONGA | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700355220 | DOC LV RECONFIG SLCP210 POLE FF58711 | 2024 | FRESHWATER | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700355233 | DOC LV RECONFIG SLCP524 POLE EP64556 | 2024 | BEECROFT | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700355246 | DOC LV RECONFIG SLCP363 POLE PY19472 | 2024 | WEST PYMBLE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700355435 | DOC LV RECONFIG SLCP377 POLE PY34661 | 2024 | LINDFIELD | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700355493 | DOC LV RECONFIG SLCPNR POLE BE85186 | 2024 | BEROWRA HEIGHTS | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700374795 | DOC LV RECONFIG SLCP7246 POLE BV01235 | 2024 | BERKELEY VALE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700392237 | DOC LV RECONFIG SLCP90 S.08943 LE33565 | 2024 | EARLWOOD | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700394666 | DOC LV RECONFIG SLCP712 POLE LE00523 | 2024 | HURLSTONE PARK | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700395161 | DOC LV RECONFIG SLCP605 POLE LE23543 | 2024 | HABERFIELD | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700520622 | DOC LV RECONFIG SLCP574 POLE LE24093 | 2024 | CROYDON | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700654626 | DOC LV RECONFIG SLCP163 POLE PY13364 | 2024 | WARRAWEE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700676347 | DOC LV RECONFIG SLCP40061 POLE LE8465 | 2024 | DULWICH HILL | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700677837 | DOC LV RECONFIG SLCP002 POLE RP17306 | 2024 | SEFTON | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700732451 | DOC LV RECONFIG SLCPNR POLE AV01851 | 2024 | COPACABANA | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700732589 | DOC LV RECONFIG SLCPNR POLE BV02199 | 2024 | BERKELEY VALE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700732615 | DOC LV RECONFIG SLCPNR POLE BV03851 | 2024 | BATEAU BAY | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700735025 | DOC LV RECONFIG SLCPNR POLE WL08684 | 2024 | BATEAU BAY | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700749136 | DOC LV RECONFIG SLCP544 S5795 | 2024 | NEWTOWN | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700749158 | DOC LV RECONFIG SLCP49 S36 | 2024 | TEMPE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.78 | Decommission CBD Vault | 1700735418 | DECOM S000912 Bligh & Bent | 2024 | SYDNEY | Several underground or vault distribution substations located in the Sydney CBD network area are no longer required, with no plans to rebuild a distribution substation on site for the foreseeable future. To prevent these sites from becoming a safety hazard for Ausgrid’s personnel and the public, there is an obligation to disconnect cables, dismantle equipment and remediate the sites.
REP_01.02.61 | Intertripping Schemes - DC | 1700438689 | REP 11KV IT PROT S000354 HASTINGS PDE | 2024 | BONDI BEACH | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.61 | Intertripping Schemes - DC | 1700438690 | REP 11KV IT PROT S000568 TECH COLLEGE NO | 2024 | ULTIMO | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.61 | Intertripping Schemes - DC | 1700438693 | REP 11KV IT PROT S001709 MOREE GORDON CE | 2024 | GORDON | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.61 | Intertripping Schemes - DC | 1700438697 | REP 11KV IT PROT S001077 TECH COLLEGE NO | 2024 | ULTIMO | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.61 | Intertripping Schemes - DC | 1700438698 | REP 11KV IT PROT S002533 GOLDMAN LANE | 2024 | DOUBLE BAY | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2024 | No Change
REP_01.03.06 | Network Protectors (West CM2/22) | 1700175812 | REP NALDER NP_1 S002502 WOOLWORTHS PARK | 2024 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2024 | No Change
REP_01.03.06 | Network Protectors (West CM2/22) | 1700175824 | REP GE OLD NP_1 S003191 AUST CLUB MACQUA | 2024 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2024 | No Change
REP_01.03.06 | Network Protectors (West CM2/22) | 1700199310 | REP WEST CM2 NP_1 S003988 ABBEY ORCHARD | 2024 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2024 | No Change
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312061 | REP NILSEN NP_1 S000074 NZ LOAN LOFTUS S | 2024 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312062 | REP NILSEN NP_2 S000074 NZ LOAN LOFTUS S | 2024 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312063 | REP NILSEN NP_3 S000074 NZ LOAN LOFTUS S | 2024 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312136 | REP WEST CM22 NP_1 S000651 PHILLIP HUNTE | 2024 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312137 | REP WEST CM22 NP_2 S000651 PHILLIP HUNTE | 2024 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312138 | REP WEST CM22 NP_3 S000651 PHILLIP HUNTE | 2024 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700437949 | REP NALDER NP_2 S002502 WOOLWORTHS PARK | 2024 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700437953 | REP GE OLD NP_2 S003191 AUST CLUB MACQUA | 2024 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700437954 | REP GE OLD NP_3 S003191 AUST CLUB MACQUA | 2024 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700437955 | REP WEST CM2 NP_2 S003988 ABBEY ORCHARD | 2024 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700437956 | REP WEST CM2 NP_3 S003988 ABBEY ORCHARD | 2024 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700438035 | REP WEST CM22 NP_1 STATE BANK ELIZABETH | 2024 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700438036 | REP WEST CM22 NP_2 STATE BANK ELIZABETH | 2024 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700438037 | REP WEST CM22 NP_3 STATE BANK ELIZABETH | 2024 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261448 | REP CBDTX_T3 S000651 Phillip Hunter | 2024 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261449 | REP CBDTX_T2 S000651 Phillip Hunter | 2024 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261450 | REP CBDTX_T1 S000651 Phillip Hunter | 2024 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700264131 | REP CBDTX_T3 S000843 Kent & King Sts | 2024 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700264132 | REP CBDTX_T2 S000843 Kent & King Sts | 2024 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700264133 | REP CBDTX_T1 S000843 Kent & King Sts | 2024 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures.
REP_01.03.13 | Bass & Saunders Isolation & Earthing Swit | 1700208983 | REP HV B&S I&E - S000651 PHILLIP HUNTER | 2024 | SYDNEY | The major issue with these assets relates to operating restrictions associated with the condition of the asset. The switch is not spring assisted and results in WH&S issues for network operators. Moreover, since their switching capacity cannot be determined, incoming feeders must be de-energised to operate the switch, which increases the time and cost of network switching. Projects have been identified based on a condition assessment.
REP_01.03.13 | Bass & Saunders Isolation & Earthing Swit | 1700208995 | REP HV B&S I&E - S000843 KENT & KING STS | 2024 | SYDNEY | The major issue with these assets relates to operating restrictions associated with the condition of the asset. The switch is not spring assisted and results in WH&S issues for network operators. Moreover, since their switching capacity cannot be determined, incoming feeders must be de-energised to operate the switch, which increases the time and cost of network switching. Projects have been identified based on a condition assessment. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_02.02.46 | SCADA Schemes - ZN & TS | 1700438533 | REP SCADA SYSTEM ZN09035 CARINGBAH | 2024 | CARINGBAH | Ausgrid has numerous unsupported proprietary SCADA systems and components installed in sub-transmission, zone and distribution substations that are now beyond their standard technical life. In all cases the maintenance and support (including replacement parts) has ceased for these legacy systems (those identified for replacement) as the hardware components are no longer available. Ausgrid’s legacy proprietary SCADA equipment also cannot support modern feeder protection relays will not support the enablement of future network capability including the Advanced Distribution Management System (ADMS). Failure of SCADA systems in zones means that visibility and controllability of the zone is lost: in the event of a fault the control room is unable to perform switching to restore supply. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_02.02.46 | SCADA Schemes - ZN & TS | 1700438612 | REP SCADA SYSTEM TS07170 SURRY HILLS STS | 2024 | SURRY HILLS | Ausgrid has numerous unsupported proprietary SCADA systems and components installed in sub-transmission, zone and distribution substations that are now beyond their standard technical life. In all cases the maintenance and support (including replacement parts) has ceased for these legacy systems (those identified for replacement) as the hardware components are no longer available. Ausgrid’s legacy proprietary SCADA equipment also cannot support modern feeder protection relays will not support the enablement of future network capability including the Advanced Distribution Management System (ADMS). Failure of SCADA systems in zones means that visibility and controllability of the zone is lost: in the event of a fault the control room is unable to perform switching to restore supply. | 2024 | No Change
REP_02.02.59 | Neutral Earthing Resistors - ZN & TS | 1700374864 | REP NER X3 TS07290 BANKSTOWN | 2024 | PADSTOW | These are approaching end of life and have hidden failure modes. Failure of these assets delays fault clearing and reduces the life of related switchgear. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_02.02.59 | Neutral Earthing Resistors - ZN & TS | 1700374867 | REP NER X3 TS07190 KURINGAI | 2024 | PYMBLE | These are approaching end of life and have hidden failure modes. Failure of these assets delays fault clearing and reduces the life of related switchgear. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_02.02.59 | Neutral Earthing Resistors - ZN & TS | 1700757027 | REP NER Y3 TS07190 KURINGAI | 2024 | PYMBLE | These are approaching end of life and have hidden failure modes. Failure of these assets delays fault clearing and reduces the life of related switchgear.
REP_02.02.59 | Neutral Earthing Resistors - ZN & TS | 1700757028 | REP NER Z3 TS07190 KURINGAI | 2024 | PYMBLE | These are approaching end of life and have hidden failure modes. Failure of these assets delays fault clearing and reduces the life of related switchgear.
REP_02.02.59 | Neutral Earthing Resistors - ZN & TS | 1700757029 | REP NER Y3 TS07290 BANKSTOWN | 2024 | PADSTOW | These are approaching end of life and have hidden failure modes. Failure of these assets delays fault clearing and reduces the life of related switchgear.
REP_02.02.59 | Neutral Earthing Resistors - ZN & TS | 1700757030 | REP NER Z3 TS07290 BANKSTOWN | 2024 | PADSTOW | These are approaching end of life and have hidden failure modes. Failure of these assets delays fault clearing and reduces the life of related switchgear.
REP_04.02.05 | LV Consac Cables (km); | 1700200733 | REP 684m CONSAC S009777_2 URANA RD W N | 2024 | YARRAWARRAH | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2024 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200786 | REP 411m CONSAC S009049_2 MARINER RD NT | 2024 | ILLAWONG | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200839 | REP 705m CONSAC S009777_1 CANOBOLAS PL | 2024 | YARRAWARRAH | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200841 | REP 649m CONSAC S009915_1 OSPREY DR WES | 2024 | ILLAWONG | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700201309 | REP 414m CONSAC S009915_2 OSPREY DR.SOU | 2024 | ILLAWONG | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700201399 | REP 130m CONSAC S000892_1 MAWSEN PDE | 2024 | CHIFLEY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700201451 | REP 262m CONSAC S003692_7 CRAIGEND ST E | 2024 | DARLINGHURST | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700201453 | REP 478m CONSAC S009174_3 WILBUNG RD WE | 2024 | ILLAWONG | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700201676 | REP 431m CONSAC S001695_3 BERESFORD RD S | 2024 | ROSE BAY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700201698 | REP 221m CONSAC S009930_2 MORETON RD EA | 2024 | ILLAWONG | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700201718 | REP 183m CONSAC S002228_1 MAROUBRA SEALS | 2024 | MAROUBRA | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700201783 | REP 134m CONSAC S005857_3 KING ST STH | 2024 | ERSKINEVILLE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700201973 | REP 146m CONSAC S002302_7 5_15 FARRELL A | 2024 | DARLINGHURST | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700201993 | REP 447m CONSAC S000602_3 HARMER ST UG | 2024 | WOOLLOOMOOLOO | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700201994 | REP 558m CONSAC S009883_2 JERVIS DR UG | 2024 | ILLAWONG | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700202188 | REP 429m CONSAC S009930_1 NORTHBROOK PL | 2024 | ILLAWONG | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700202204 | REP 738m CONSAC S009244_1 TURRELLA RD W | 2024 | YARRAWARRAH | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700202205 | REP 635m CONSAC S009341_3 MORETON RD SO | 2024 | ILLAWONG | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700202207 | REP 700m CONSAC S009883_1 JERVIS GERALD | 2024 | ILLAWONG | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700202208 | REP 747m CONSAC S002143_1 O SULLIVAN RD | 2024 | ROSE BAY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700202233 | REP 349m CONSAC S009603_1 BLAXLAND DR S | 2024 | ILLAWONG | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700202234 | REP 262m CONSAC S009603_2 BLAXLAND DR N | 2024 | ILLAWONG | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700202235 | REP 330m CONSAC S009049_3 MARINER RD ST | 2024 | ILLAWONG | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700202641 | REP 465m CONSAC S009257_1 AUSTIN ST | 2024 | ILLAWONG | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700202809 | REP 409m CONSAC S009355_1 GILES ST UG | 2024 | YARRAWARRAH | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700202998 | REP 512m CONSAC S009417_2 REDMAN AVE | 2024 | ILLAWONG | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700202999 | REP 562m CONSAC S009417_1 FIELD PL | 2024 | ILLAWONG | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700203107 | REP 281m CONSAC S009941_1 SHEOAK PL UG | 2024 | ALFORDS POINT | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700203222 | REP 687m CONSAC S009341_1 MORETON RD NO | 2024 | ILLAWONG | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700203223 | REP 485m CONSAC S009174_2 WILBUNG RD EAS | 2024 | ILLAWONG | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700203651 | REP 443m CONSAC S009916_1 OSPREY DR.EAS | 2024 | ILLAWONG | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700203652 | REP 541m CONSAC S009600_2 HOBART PL UG | 2024 | ILLAWONG | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700203653 | REP 455m CONSAC S009168_2 HERITAGE DR ST | 2024 | ILLAWONG | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700203654 | REP 528m CONSAC S009600_3 OLD FERRY RD O | 2024 | ILLAWONG | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700203701 | REP 164m CONSAC S004214_2 JOHN ST & NO | 2024 | ASHFIELD | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700203724 | REP 134m CONSAC S000184_2 LUGAR BRAE AV | 2024 | WAVERLEY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700203888 | REP 219m CONSAC S009941_2 COACHWOOD CRE | 2024 | ALFORDS POINT | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700204552 | REP 375m CONSAC S009259_1 BLAXLAND DR.U | 2024 | ILLAWONG | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700204553 | REP 367m CONSAC S009257_2 REDMAN AVE | 2024 | ILLAWONG | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700204554 | REP 380m CONSAC S009174_1 MORETON RD UG | 2024 | ILLAWONG | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700204558 | REP 322m CONSAC S009883_3 ORIANA DRIVE | 2024 | ILLAWONG | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700204559 | REP 345m CONSAC S009341_2 CYGNET PL U G | 2024 | ILLAWONG | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700204660 | REP 152m CONSAC S003692_1 CRAIGEND ST & | 2024 | DARLINGHURST | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700204767 | REP 149m CONSAC S009259_3 BLAXLAND DRIV | 2024 | ILLAWONG | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700204948 | REP 293m CONSAC S009916_2 OSPREY DR.WES | 2024 | ILLAWONG | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700204949 | REP 259m CONSAC S009983_1 SPROULE RD WE | 2024 | ILLAWONG | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700204950 | REP 374m CONSAC S009417_3 AUSTIN ST NOR | 2024 | ILLAWONG | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700204952 | REP 256m CONSAC S009044_2 MONTAGUE ST U | 2024 | ILLAWONG | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700205121 | REP 130m CONSAC S009917_2 OCEAN PL UG | 2024 | ILLAWONG | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700205153 | REP 305m CONSAC PT11918_1 GLENROCK PDE N | 2024 | KOOLEWONG | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700205324 | REP 158m CONSAC S000602_6 FORBES ST UG | 2024 | WOOLLOOMOOLOO | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700205400 | REP 131m CONSAC S009044_1 BLAXLAND DV.U | 2024 | ILLAWONG | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700205966 | REP 141m CONSAC S001520_3 PARRAMATTA ROA | 2024 | LEICHHARDT | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700214272 | REP 371m CONSAC HS78480_1 MALANG NORFOLK | 2024 | ASHTONFIELD | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2024 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700214273 | REP 187m CONSAC HS78480_2 MALANG NORFOL | 2024 | ASHTONFIELD | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2024 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700214274 | REP 306m CONSAC HS78480_3 MALANG NORFOLK | 2024 | ASHTONFIELD | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2024 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700214275 | REP 256m CONSAC HS78480_4 MALANG NORFOLK | 2024 | ASHTONFIELD | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2024 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700214277 | REP 491m CONSAC HS52120_1 FERN PLACE | 2024 | EAST MAITLAND | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2024 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700214278 | REP 478m CONSAC HS52120_2 FERN PLACE | 2024 | EAST MAITLAND | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2024 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700214279 | REP 217m CONSAC HS52120_3 FERN PLACE | 2024 | EAST MAITLAND | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2024 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700214280 | REP 134m CONSAC HS52120_4 FERN PLACE | 2024 | EAST MAITLAND | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2024 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700715344 | REP 250m CONSAC HS13269/13274 Cbl Jnt | 2024 | JEWELLS | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.06 | Low Voltage HDPE Cables (km) | 1700241348 | REP 143m HDPE S007370_2 MAROUBRA RD | 2024 | MAROUBRA | Ausgrid has approximately 110km of LV HDPE cable installed on its distribution network, which was installed between the mid 1970s until the mid 1980s. Ausgrid's HDPE LV cables have higher failure rates than other types of LV cable on the network. The need to replace HDPE cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all HDPE cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.06 | Low Voltage HDPE Cables (km) | 1700245555 | REP 151m HDPE S001030_1 MATRAVILLE RSL | 2024 | MATRAVILLE | Ausgrid has approximately 110km of LV HDPE cable installed on its distribution network, which was installed between the mid 1970s until the mid 1980s. Ausgrid's HDPE LV cables have higher failure rates than other types of LV cable on the network. The need to replace HDPE cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all HDPE cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.06 | Low Voltage HDPE Cables (km) | 1700440426 | REP 386m HDPE S077006_1 DARLEY RD W UG | 2024 | MANLY | Ausgrid has approximately 110km of LV HDPE cable installed on its distribution network, which was installed between the mid 1970s until the mid 1980s. Ausgrid's HDPE LV cables have higher failure rates than other types of LV cable on the network. The need to replace HDPE cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all HDPE cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.06 | Low Voltage HDPE Cables (km) | 1700440428 | REP 455m HDPE S077006_2 DARLEY RD E UG | 2024 | MANLY | Ausgrid has approximately 110km of LV HDPE cable installed on its distribution network, which was installed between the mid 1970s until the mid 1980s. Ausgrid's HDPE LV cables have higher failure rates than other types of LV cable on the network. The need to replace HDPE cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all HDPE cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.06 | Low Voltage HDPE Cables (km) | 1700440432 | REP 148m HDPE S016427_4 EAST ESPLANADE W | 2024 | MANLY | Ausgrid has approximately 110km of LV HDPE cable installed on its distribution network, which was installed between the mid 1970s until the mid 1980s. Ausgrid's HDPE LV cables have higher failure rates than other types of LV cable on the network. The need to replace HDPE cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all HDPE cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.06 | Low Voltage HDPE Cables (km) | 1700487933 | REP 175m HDPE S015087_3 ASHBURNER ST UG | 2024 | MANLY | Ausgrid has approximately 110km of LV HDPE cable installed on its distribution network, which was installed between the mid 1970s until the mid 1980s. Ausgrid's HDPE LV cables have higher failure rates than other types of LV cable on the network. The need to replace HDPE cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all HDPE cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700438211 | REP TWR 20 IU58020 FDR 960/961 | 2024 | ARGENTON | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700438212 | REP TWR 21 IU58021 FDR 960/961 | 2024 | ARGENTON | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700438213 | REP TWR 23 IU58023 FDR 960/961 | 2024 | ARGENTON | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700438214 | REP TWR 22 IU58022 FDR 960/961 | 2024 | ARGENTON | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700438215 | REP TWR 24 IU58024 FDR 960/961 | 2024 | CARDIFF | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700488365 | REP TWR 53 JU78053 FDR 960/961 | 2024 | ADAMSTOWN | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700642449 | REP TOWER CR9138 FDR 916/917 | 2024 | KURNELL | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700642450 | REP TOWER CR9137 FDR 916/917 | 2024 | WOOLOOWARE | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700642451 | REP TOWER CR9136 FDR 916/917 | 2024 | WOOLOOWARE | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700642452 | REP TOWER CR9135 FDR 916/917 | 2024 | WOOLOOWARE | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700642453 | REP TOWER CR9134 FDR 916/917 | 2024 | WOOLOOWARE | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700643381 | REP TOWER 17 IU58017 FDR 960/961 | 2024 | BARNSLEY | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700643383 | REP TOWER 16 IU58016 FDR 960/961 | 2024 | BARNSLEY | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2024 | No Change
REP_05.02.01-5 | Tower Replacement | 1700643386 | REP TOWER 18 IU58018 FDR 960/961 | 2024 | BARNSLEY | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2024 | No Change
REP_05.02.01-5 | Tower Replacement | 1700643387 | REP TOWER 19 IU58019 FDR 960/961 | 2024 | BARNSLEY | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700643388 | REP TOWER 14 IU48014 FDR 960/961 | 2024 | BARNSLEY | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700643389 | REP TOWER 15 IU48015 FDR 960/961 | 2024 | BARNSLEY | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700643924 | REP TWR 40 IU98040 960/961 | 2024 | HILLSBOROUGH | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700674788 | REP TOWER 54 CR09131 FDR 916/917 | 2024 | WOOLOOWARE | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option.
REP_05.02.01-5 | Tower Replacement | 1700674789 | REP TOWER 55 CR09132 FDR 916/917 | 2024 | WOOLOOWARE | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option.
REP_05.02.01-5 | Tower Replacement | 1700674797 | REP TOWER 52 CR09129 FDR 916/917 | 2024 | WOOLOOWARE | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option.
REP_05.02.01-5 | Tower Replacement | 1700674798 | REP TOWER 53 CR09130 FDR 916/917 | 2024 | WOOLOOWARE | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option.
REP_05.02.01-5 | Tower Replacement | 1700674799 | REP TOWER 56 CR09133 FDR 916/917 | 2024 | WOOLOOWARE | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354224 | DOC LV RECONFIG SLCP871 POLE PA79949 | 2025 | DENISTONE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354226 | DOC LV RECONFIG SLCP826 POLE GL65870 | 2025 | ROSEVILLE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354227 | DOC LV RECONFIG SLCP1192 POLE GL94052 | 2025 | RIVERVIEW | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354231 | DOC LV RECONFIG SLCP3045 POLE BA00501 | 2025 | LILLI PILLI | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354248 | 0.300V RECONFIG SLCP354 POLE MO30407 | 2025 | BALGOWLAH | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354249 | DOC LV RECONFIG SLCP192 POLE MO92088 | 2025 | CASTLECRAG | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354253 | DOC LV RECONFIG SLCP363 POLE MO31132 | 2025 | SEAFORTH | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354257 | DOC LV RECONFIG SLCP876 POLE RP20004 | 2025 | CONDELL PARK | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354264 | DOC LV RECONFIG SLCP921 POLE EP13303 | 2025 | WESTLEIGH | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354267 | DOC LV RECONFIG SLCP1568 POLE PA82833 | 2025 | EASTWOOD | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354276 | DOC LV RECONFIG SLCP909 POLE SY12867 | 2025 | COOGEE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354287 | DOC LV RECONFIG SLCP719 POLE GL90890 | 2025 | CHATSWOOD | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354296 | DOC LV RECONFIG SLCP157 POLE GL57886 | 2025 | HUNTERS HILL | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354299 | DOC LV RECONFIG SLCPNR POLE CR06923 | 2025 | SYLVANIA WATERS | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354304 | DOC LV RECONFIG SLCP1025 POLE MC15712 | 2025 | WAHROONGA | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354311 | DOC LV RECONFIG SLCP106 POLE LR11450 | 2025 | NARRABEEN | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354319 | DOC LV RECONFIG SLCP19 POLE PY20216 | 2025 | TURRAMURRA | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354322 | DOC LV RECONFIG SLCP1241 POLE MC06107 | 2025 | ASQUITH | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354326 | DOC LV RECONFIG SLCP195 POLE MO27244 | 2025 | NORTHBRIDGE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354328 | DOC LV RECONFIG SLCP599 POLE GL54846 | 2025 | RYDE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354334 | DOC LV RECONFIG SLCP872 POLE PY30646 | 2025 | MARSFIELD | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354335 | DOC LV RECONFIG SLCP518 POLE EP81177 | 2025 | CARLINGFORD | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354337 | DOC LV RECONFIG SLCP6592 POLE BA01498 | 2025 | CRONULLA | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354343 | DOC LV RECONFIG SLCP170 POLE MC14414 | 2025 | TURRAMURRA | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354349 | DOC LV RECONFIG SLCP1337 POLE MC01633 | 2025 | MOUNT COLAH | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354355 | 4DOC LV RECONFIG SLCP3102 POLE SU05918 | 2025 | BONNET BAY | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354360 | DOC LV RECONFIG SLCP3024 POLE CR08661 | 2025 | SYLVANIA | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354361 | DOC LV RECONFIG SLCP3012 POLE SU01785 | 2025 | ENGADINE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354378 | DOC LV RECONFIG SLCP3049 POLE CR00988 | 2025 | WOOLOOWARE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354382 | DOC LV RECONFIG SLCP3342 POLE KO14060 | 2025 | BARDWELL PARK | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354386 | DOC LV RECONFIG SLCP1239 POLE MC01484 | 2025 | MOUNT COLAH | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354387 | DOC LV RECONFIG SLCP897 POLE GL70707 | 2025 | RYDE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354388 | DOC LV RECONFIG SLCP969 POLE RP23679 | 2025 | BERALA | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354400 | DOC LV RECONFIG SLCP405 POLE EP24347 | 2025 | EASTWOOD | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354402 | DOC LV RECONFIG SLCP3043 POLE CR03974 | 2025 | CARINGBAH | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354407 | DOC LV RECONFIG SLCP499 POLE EP78312 | 2025 | EPPING | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354410 | DOC LV RECONFIG SLCP3011 POLE EN00405 | 2025 | ENGADINE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354420 | DOC LV RECONFIG SLCP549 POLE GL35070 | 2025 | NORTH RYDE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354423 | DOC LV RECONFIG SLCP207 POLE MO69941 | 2025 | NAREMBURN | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354425 | DOC LV RECONFIG SLCP536 POLE MO02212 | 2025 | NORTH WILLOUGHBY | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354437 | DOC LV RECONFIG SLCP1193 POLE GL72474 | 2025 | DENISTONE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354438 | DOC LV RECONFIG SLCP1059 POLE PA74272 | 2025 | EASTWOOD | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354441 | DOC LV RECONFIG SLCP3058 POLE KL00203 | 2025 | KURNELL | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354442 | DOC LV RECONFIG SLCP665 POLE RP05887 | 2025 | STRATHFIELD | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354443 | DOC LV RECONFIG SLCPNR POLE PA02594 | 2025 | SILVERWATER | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354454 | DOC LV RECONFIG SLCP205 POLE GL94667. | 2025 | GREENWICH | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354458 | DOC LV RECONFIG SLCP509 POLE EP78191 | 2025 | EPPING | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354466 | DOC LV RECONFIG SLCP3035 POLE SU13079 | 2025 | GYMEA BAY | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354479 | DOC LV RECONFIG SLCP519 POLE GL33045 | 2025 | NORTH RYDE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354491 | DOC LV RECONFIG SLCP146 POLE PY31755 | 2025 | EASTWOOD | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354492 | DOC LV RECONFIG SLCP389 POLE SY06982 | 2025 | ROSEBERY | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354501 | DOC LV RECONFIG SLCP3076 POLE SU15210 | 2025 | GYMEA | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354502 | DOC LV RECONFIG SLCP3096 POLE SU12224 | 2025 | KAREELA | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354504 | DOC LV RECONFIG SLCP356 POLE GL04369 | 2025 | CONCORD | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354509 | DOC LV RECONFIG SLCP313 POLE GL48936. | 2025 | GLADESVILLE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354513 | DOC LV RECONFIG SLCP717 POLE EP76987 | 2025 | CARLINGFORD | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354518 | DOC LV RECONFIG SLCP3054 POLE CR04729 | 2025 | WOOLOOWARE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354524 | DOC LV RECONFIG SLCP3135 POLE CR10060 | 2025 | KURNELL | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354532 | DOC LV RECONFIG SLCP323 POLE GL33304 | 2025 | NORTH RYDE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354538 | DOC LV RECONFIG SLCP510 POLE MC08551 | 2025 | WAITARA | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354545 | DOC LV RECONFIG SLCP3050 POLE CR00564 | 2025 | CARINGBAH | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354548 | DOC LV RECONFIG SLCP3047 POLE CR03936 | 2025 | CARINGBAH | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354557 | DOC LV RECONFIG SLCP689 POLE GL35004 | 2025 | RYDE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354558 | DOC LV RECONFIG SLCP515 POLE EP76639 | 2025 | EPPING | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354561 | DOC LV RECONFIG SLCP3120 POLE SU02658 | 2025 | ENGADINE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354565 | DOC LV RECONFIG SLCP388 POLE. GL54498 | 2026 | GLADESVILLE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354577 | DOC LV RECONFIG SLCP3027 POLE SU09799 | 2026 | LOFTUS | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354591 | DOC LV RECONFIG SLCP3064 POLE SU15461 | 2026 | KIRRAWEE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354599 | DOC LV RECONFIG SLCP412 POLE EP74023 | 2026 | NORTH EPPING | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354611 | DOC LV RECONFIG SLCP310 POLE MA11362 | 2026 | MAROUBRA | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354623 | DOC LV RECONFIG SLCP3015 POLE EN01762 | 2026 | HEATHCOTE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354625 | DOC LV RECONFIG SLCP7113 POLE GO01433 | 2026 | WYOMING | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354627 | DOC LV RECONFIG SLCP3088 POLE SU14272 | 2026 | GYMEA | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354635 | DOC LV RECONFIG SLCP3576 POLE SU02783 | 2026 | LOFTUS | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354639 | DOC LV RECONFIG SLCP823 POLE SY19255 | 2026 | RANDWICK | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354654 | DOC LV RECONFIG SLCP3025 POLE SU10882 | 2026 | OYSTER BAY | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354686 | DOC LV RECONFIG SLCP523 POLE EP17340 | 2026 | PENNANT HILLS | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354691 | DOC LV RECONFIG SLCP350 POLE MO25594 | 2026 | BALGOWLAH HEIGHTS | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354692 | DOC LV RECONFIG SLCP3358 POLE KO03985 | 2026 | BEXLEY | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354736 | DOC LV RECONFIG SLCP339 POLE PA79535 | 2026 | WEST RYDE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354739 | DOC LV RECONFIG SLCP178 POLE PY19293 | 2026 | TURRAMURRA | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354749 | DOC LV RECONFIG SLCP3029 POLE SU00740 | 2026 | COMO | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354758 | DOC LV RECONFIG SLCP607 POLE PA85481 | 2026 | EASTWOOD | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354761 | DOC LV RECONFIG SLCP830 POLE GL50801 | 2026 | EAST RYDE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354763 | DOC LV RECONFIG SLCP1159 POLE RP27250 | 2026 | STRATHFIELD SOUTH | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354772 | DOC LV RECONFIG SLCP369 POLE MA00797 | 2026 | CHIFLEY | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354778 | DOC LV RECONFIG SLCP3059 POLE BA00721 | 2026 | BURRANEER | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354798 | DOC LV RECONFIG SLCP287 POLE GL51081 | 2026 | GLADESVILLE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354806 | DOC LV RECONFIG SLCP1456 POLE GL73147 | 2026 | HENLEY | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354846 | DOC LV RECONFIG SLCP344 POLE MO40452 | 2026 | SEAFORTH | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354881 | DOC LV RECONFIG SLCP3052 POLE BA02208 | 2026 | BUNDEENA | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354886 | DOC LV RECONFIG SLCP573 POLE MO47770 | 2026 | NORTHBRIDGE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354899 | DOC LV RECONFIG SLCP3048 POLE CR05503 | 2026 | CARINGBAH SOUTH | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354904 | DOC LV RECONFIG SLCP3077 POLE SU15276 | 2026 | KIRRAWEE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354908 | DOC LV RECONFIG SLCP1094 POLE FA00876 | 2026 | CHESTER HILL | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354914 | DOC LV RECONFIG SLCP442 POLE FF19898 | 2026 | FRENCHS FOREST | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354917 | DOC LV RECONFIG SLCP706 POLE PY18262 | 2026 | TURRAMURRA | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354926 | DOC LV RECONFIG SLCP3078 POLE SU11842 | 2026 | KIRRAWEE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354933 | DOC LV RECONFIG SLCP3018 POLE SU05173 | 2026 | SUTHERLAND | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354950 | DOC LV RECONFIG SLCP3034 POLE SU14116 | 2026 | MIRANDA | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354982 | DOC LV RECONFIG SLCP3101 POLE CR05693 | 2026 | SYLVANIA WATERS | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354983 | DOC LV RECONFIG SLCP720 POLE MO78723 | 2026 | CHATSWOOD | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354986 | DOC LV RECONFIG SLCP3095 POLE SU02460 | 2026 | ENGADINE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700355000 | DOC LV RECONFIG SLCP320 POLE PA69639 | 2026 | WEST RYDE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700355038 | DOC LV RECONFIG SLCP3021 POLE SU11949 | 2026 | KIRRAWEE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700355044 | DOC LV RECONFIG SLCP3044 POLE CR04225 | 2026 | CARINGBAH SOUTH | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700355054 | DOC LV RECONFIG SLCP433 POLE PA82789. | 2026 | EASTWOOD | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700355098 | DOC LV RECONFIG SLCP978 POLE GL34888 | 2027 | RYDE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700355101 | DOC LV RECONFIG SLCP3009 POLE SU04718 | 2027 | LOFTUS | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700355109 | DOC LV RECONFIG SLCP512 POLE LE12758 | 2027 | BALMAIN | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700355130 | DOC LV RECONFIG SLCP3031 POLE CR06153 | 2027 | SYLVANIA | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2027 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700355138 | DOC LV RECONFIG SLCP3203 POLE SU11687 | 2027 | SYLVANIA | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2027 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700355142 | DOC LV RECONFIG SLCP1134 POLE EH02701 | 2027 | PANANIA | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2027 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700355150 | DOC LV RECONFIG SLCP3091 POLE CR02543 | 2027 | CARINGBAH | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2027 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700355197 | DOC LV RECONFIG SLCP172 POLE FF82409 | 2027 | NARRAWEENA | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2027 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700355222 | DOC LV RECONFIG SLCP1310 POLE GL38026 | 2027 | LANE COVE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2027 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700355241 | DOC LV RECONFIG SLCP3087 POLE EN01531 | 2027 | HEATHCOTE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2027 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700355282 | DOC LV RECONFIG SLCP3057 POLE CR02439 | 2027 | CRONULLA | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2027 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700355299 | DOC LV RECONFIG SLCP3046 POLE CR07098 | 2027 | CARINGBAH SOUTH | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2027 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700355311 | DOC LV RECONFIG SLCP3041 POLE CR01494 | 2027 | CARINGBAH | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2027 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700355321 | DOC LV RECONFIG SLCP3037 POLE CR07127 | 2027 | YOWIE BAY | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2027 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700355331 | DOC LV RECONFIG SLCP888 POLE GL41594 | 2027 | RYDE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2027 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700355385 | DOC LV RECONFIG SLCP3119 POLE CR05569 | 2027 | MIRANDA | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2027 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700355542 | DOC LV RECONFIG SLCP1026 POLE PY23441. | 2027 | MARSFIELD | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2027 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700355585 | DOC LV RECONFIG SLCP3019 POLE SU14741 | 2027 | KIRRAWEE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2027 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700514293 | DOC LV RECONFIG SLCP44 SUB S000440 | 2027 | STRATHFIELD | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2027 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700355727 | DOC LV RECONFIG SLCP3014 POLE EN01846 | 2027 | HEATHCOTE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2027 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700355758 | DOC LV RECONFIG SLCP23 POLE EP81828 | 2027 | WEST PENNANT HILLS | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2027 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700355798 | DOC LV RECONFIG SLCP3007 POLE SU04553 | 2027 | SUTHERLAND | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2027 | No Change
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700721169 | DOC LV RECONFIG SLCP1738_S5770_LE10805 | 2027 | GLEBE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700356591 | DOC LV RECONFIG SLCP5 POLE BA00553 | 2027 | LILLI PILLI | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700732549 | DOC LV RECONFIG SLCPNR POLE BU02274 | 2027 | SAN REMO | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700732550 | DOC LV RECONFIG SLCPNR POLE BU02612 | 2027 | HALEKULANI | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700732624 | DOC LV RECONFIG SLCPNR POLE BV04355 | 2028 | KILLARNEY VALE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700732637 | DOC LV RECONFIG SLCPNR POLE CH00184 | 2028 | GWANDALAN | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700732780 | DOC LV RECONFIG SLCPNR POLE EP22595 | 2028 | EASTWOOD | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700394251 | DOC LV RECONFIG SLCP866 POLE PE10833 | 2028 | RIVERWOOD | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700394254 | DOC LV RECONFIG SLCP1780 SUB.05973 | 2028 | BANKSTOWN | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700394255 | DOC LV RECONFIG SLCP137 SUB.01279 | 2028 | CHESTER HILL | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700394682 | DOC LV RECONFIG SLCP988 SUB S001880 | 2028 | BELMORE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700379056 | DOC LV RECONFIG SLCP38 POLE RP00545 | 2028 | STRATHFIELD | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700379237 | DOC LV RECONFIG SLCP1396 POLE PE07845 | 2028 | BELMORE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700549605 | DOC LV RECONFIG SLCP125 POLE EH01065 | 2028 | MILPERRA | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700396421 | DOC LV RECONFIG SLCP84 POLE LE21780 | 2028 | CROYDON PARK | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700438106 | DOC LV RECONFIG SLCP545 POLE LE13426 | 2028 | BALMAIN | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700440632 | DOC LV RECONFIG SLCP887 SUB S000682 | 2028 | LEICHHARDT | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700475937 | DOC LV RECONFIG SLCP1341 S4583 | 2028 | REVESBY | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700457609 | DOC LV RECONFIG SLCP655 PE16800 | 2028 | REVESBY | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700444174 | DOC LV RECONFIG SLCP1406 SUB S000672 | 2028 | STRATHFIELD | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700487973 | DOC LV RECONFIG SLCP1709 SUB5169 | 2028 | STRATHFIELD SOUTH | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700505209 | DOC LV RECONFIG SLCP351 POLE MO28803 | 2028 | BALGOWLAH | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700734917 | DOC LV RECONFIG SLCPNR POLE TO01774 | 2028 | WYONGAH | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700734921 | DOC LV RECONFIG SLCPNR POLE TO02535 | 2028 | TOUKLEY | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700734951 | DOC LV RECONFIG SLCPNR POLE VP00707 | 2028 | MANNERING PARK | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700735056 | DOC LV RECONFIG SLCPNR POLE WW04205 | 2028 | TASCOTT | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700735065 | DOC LV RECONFIG SLCPNR POLE WW04809 | 2028 | UMINA BEACH | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700735085 | DOC LV RECONFIG SLCPNR POLE WY01251 | 2028 | WYONG | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.78 | Decommission CBD Vault | 1700735415 | DECOM S000431 Elizabeth St St James | 2025 | SYDNEY | Several underground or vault distribution substations located in the Sydney CBD network area are no longer required, with no plans to rebuild a distribution substation on site for the foreseeable future. To prevent these sites from becoming a safety hazard for Ausgrid’s personnel and the public, there is an obligation to disconnect cables, dismantle equipment and remediate the sites.
DOC_11.03.78 | Decommission CBD Vault | 1700735417 | DECOM S000428 Bridge & George | 2026 | SYDNEY | Several underground or vault distribution substations located in the Sydney CBD network area are no longer required, with no plans to rebuild a distribution substation on site for the foreseeable future. To prevent these sites from becoming a safety hazard for Ausgrid’s personnel and the public, there is an obligation to disconnect cables, dismantle equipment and remediate the sites.
REP_01.02.61 | Intertripping Schemes - DC | 1700438688 | REP 11KV IT PROT S000123 JOHNSON QUEEN | 2025 | ALEXANDRIA | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.61 | Intertripping Schemes - DC | 1700438696 | REP 11KV IT PROT S002420 BANKSTOWN SQUAR | 2025 | BANKSTOWN | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.61 | Intertripping Schemes - DC | 1700438701 | REP 11KV IT PROT S002582 ANZAC WAL | 2025 | KINGSFORD | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2025 | No Change
REP_01.02.61 | Intertripping Schemes - DC | 1700438702 | REP 11KV IT PROT S002797 FREDERICK HERBE | 2025 | ARTARMON | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2025 | No Change
REP_01.02.61 | Intertripping Schemes - DC | 1700438704 | REP 11KV IT PROT S003002 ARTHUR MOUNT NO | 2025 | NORTH SYDNEY | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2025 | No Change
REP_01.02.61 | Intertripping Schemes - DC | 1700438705 | REP 11KV IT PROT S002975 CLIFF LAVENDER | 2025 | MILSONS POINT | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2025 | No Change
REP_01.02.61 | Intertripping Schemes - DC | 1700438706 | REP 11KV IT PROT S002959 KIPPAX HOLT NO | 2026 | SURRY HILLS | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2026 | No Change
REP_01.02.61 | Intertripping Schemes - DC | 1700438707 | REP 11KV IT PROT S003239 MEREWETHER BUIL | 2026 | DARLINGTON | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2026 | No Change
REP_01.02.61 | Intertripping Schemes - DC | 1700438708 | REP 11KV IT PROT S003237 PENNYS LANE | 2026 | POTTS POINT | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2026 | No Change
REP_01.02.61 | Intertripping Schemes - DC | 1700438709 | REP 11KV IT PROT S003167 NEW MCLEAN ST | 2026 | EDGECLIFF | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2026 | No Change
REP_01.02.61 | Intertripping Schemes - DC | 1700438710 | REP 11KV IT PROT S003542 LOVE NB NO 1 | 2026 | STRATHFIELD SOUTH | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2026 | No Change
REP_01.02.61 | Intertripping Schemes - DC | 1700438711 | REP 11KV IT PROT S003554 ROBINSON PALM | 2026 | WOOLLOOMOOLOO | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2026 | No Change
REP_01.02.61 | Intertripping Schemes - DC | 1700438712 | REP 11KV IT PROT S003680 MCLAREN NORTHSI | 2027 | NORTH SYDNEY | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2027 | No Change
REP_01.02.61 | Intertripping Schemes - DC | 1700438713 | REP 11KV IT PROT S003718 HILL AGL CENTRE | 2027 | NORTH SYDNEY | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2027 | No Change
REP_01.02.61 | Intertripping Schemes - DC | 1700438714 | REP 11KV IT PROT S002960 KIPPAX HOLT NO. | 2027 | SURRY HILLS | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2027 | No Change
REP_01.02.61 | Intertripping Schemes - DC | 1700438715 | REP 11KV IT PROT S003666 MECH. ENGINEERI | 2027 | DARLINGTON | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2027 | No Change
REP_01.02.61 | Intertripping Schemes - DC | 1700438716 | REP 11KV IT PROT S003646 WEMYSS WENT | 2027 | SURRY HILLS | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2027 | No Change
REP_01.02.61 | Intertripping Schemes - DC | 1700438717 | REP 11KV IT PROT S004091 LIVERPOOL NITH | 2027 | SYDNEY | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2027 | No Change
REP_01.02.61 | Intertripping Schemes - DC | 1700438718 | REP 11KV IT PROT S003915 MILLER NORTHPOI | 2028 | NORTH SYDNEY | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life.
REP_01.02.61 | Intertripping Schemes - DC | 1700438719 | REP 11KV IT PROT S003762 GEORGE PORT | 2028 | WATERLOO | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life.
REP_01.02.61 | Intertripping Schemes - DC | 1700438720 | REP 11KV IT PROT S004186 EASTWOOD SHOPPI | 2028 | EASTWOOD | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life.
REP_01.02.61 | Intertripping Schemes - DC | 1700438721 | REP 11KV IT PROT S003692 NIMROD ST | 2028 | DARLINGHURST | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life.
REP_01.02.61 | Intertripping Schemes - DC | 1700438722 | REP 11KV IT PROT S004590 CARROLL LANE | 2028 | BONDI JUNCTION | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life.
REP_01.02.61 | Intertripping Schemes - DC | 1700438724 | REP 11KV IT PROT S005325 WATERLOO MACQUA | 2028 | MACQUARIE PARK | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700175810 | REP NALDER NP_1 S000843 KENT & KING STS | 2025 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700175815 | REP NALDER NP_1 S000414 CLARENCE MARGARE | 2025 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700311949 | REP NALDER NP_2 S000414 CLARENCE & MARGA | 2025 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700311953 | REP NALDER NP_2 S000843 KENT & KING STS | 2025 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700311950 | REP NALDER NP_3 S000414 CLARENCE & MARGA | 2025 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700311954 | REP NALDER NP_3 S000843 KENT & KING STS | 2025 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700175825 | REP GE OLD NP_1 S000428 BRIDGE & GEORGE | 2025 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700283779 | REP WEST CM2 NP_1 S001022 GOULBURN & ELI | 2025 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700288075 | DEC GE MG9 NP_1 S000840 PITT ST STRAND A | 2025 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700311988 | REP WEST CM2 NP_1 S000842 CASTLEREAGH & | 2025 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700311989 | REP WEST CM2 NP_2 S000842 CASTLEREAGH & | 2025 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700311992 | REP WEST CM2 NP_3 S001022 GOULBURN & ELI | 2025 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700311990 | REP WEST CM2 NP_3 S000842 CASTLEREAGH & | 2025 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700311996 | REP WEST CM2 NP_1 S001036 KING ST SYDNEY | 2025 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700311997 | REP WEST CM2 NP_2 S001036 KING ST SYDNEY | 2025 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700311998 | REP WEST CM2 NP_3 S001036 KING ST SYDNEY | 2026 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312002 | REP WEST CM2 NP_1 S001903 JAMES HARDIE A | 2026 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312003 | REP WEST CM2 NP_2 S001903 JAMES HARDIE A | 2026 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312009 | REP GE OLD NP_2 S000428 BRIDGE & GEORGE | 2026 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312010 | REP GE OLD NP_3 S000428 BRIDGE & GEORGE | 2026 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312016 | REP GE MG9 NP_2 S000840 PITT ST STRAND A | 2026 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312017 | REP GE OLD NP_3 S000840 PITT ST STRAND A | 2026 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312021 | REP GE OLD NP_1 S001019 O'CONNELL ST BRO | 2026 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312022 | REP GE OLD NP_2 S001019 O'CONNELL ST BRO | 2026 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312023 | REP GE OLD NP_3 S001019 O'CONNELL ST BRO | 2026 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312024 | REP GE OLD NP_1 S001020 KENT & MARKET ST | 2026 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312025 | REP GE OLD NP_2 S001020 KENT & MARKET ST | 2026 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312026 | REP GE OLD NP_3 S001020 KENT & MARKET ST | 2026 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312027 | REP GE MG9 NP_1 S001339 PITT ST ADAMS HO | 2026 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312028 | REP GE MG9 NP_2 S001339 PITT ST ADAMS HO | 2026 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312029 | REP GE MG9 NP_3 S001339 PITT ST ADAMS HO | 2026 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312033 | REP GE OLD NP_1 S002028 LA SALLE KING ST | 2027 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312034 | REP GE OLD NP_2 S002028 LA SALLE KING ST | 2027 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312035 | REP GE OLD NP_3 S002028 LA SALLE KING ST | 2027 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312043 | REP NILSEN NP_1 S000427 O'CONNELL & HUNT | 2027 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312044 | REP NILSEN NP_2 S000427 O'CONNELL & HUNT | 2027 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312045 | REP NILSEN NP_3 S000427 O'CONNELL & HUNT | 2027 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700288073 | DEC WEST CM2 NP_1 S000430 BATHURST & KE | 2027 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312049 | REP NILSEN NP_1 S000856 PITT & HUNTER ST | 2027 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312050 | REP NILSEN NP_2 S000856 PITT & HUNTER ST | 2027 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312051 | REP NILSEN NP_3 S000856 PITT & HUNTER ST | 2027 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312055 | REP NILSEN NP_1 S004016 EXCHGE CTR PITT | 2027 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312056 | REP NILSEN NP_2 S004016 EXCHGE CTR PITT | 2027 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312057 | REP NILSEN NP_3 S004016 EXCHGE CTR PITT | 2027 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312070 | REP WEST CM22 NP_2 S000430 BATHURST & KE | 2027 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312071 | REP WEST CM22 NP_3 S000430 BATHURST & KE | 2027 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312072 | REP WEST CM22 NP_1 S000431 ELIZ ST ST JA | 2027 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312073 | REP WEST CM22 NP_2 S000431 ELIZ ST ST JA | 2028 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312074 | REP WEST CM22 NP_3 S000431 ELIZ ST ST JA | 2028 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312075 | REP WEST CM22 NP_1 S000541 DRUITT & CLAR | 2028 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312076 | REP WEST CM22 NP_2 S000541 DRUITT & CLAR | 2028 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312077 | REP WEST CM22 NP_3 S000541 DRUITT & CLAR | 2028 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312096 | REP WEST CM22 NP_1 S000908 CASTLERGH & H | 2028 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312097 | REP WEST CM22 NP_2 S000908 CASTLERGH & H | 2028 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312098 | REP WEST CM22 NP_3 S000908 CASTLERGH & H | 2028 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312099 | REP WEST CM22 NP_1 S000912 BLIGH & BENT | 2028 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312100 | REP WEST CM22 NP_2 S000912 BLIGH & BENT | 2028 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312101 | REP WEST CM22 NP_3 S000912 BLIGH & BENT | 2028 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312113 | REP WEST CM22 NP_1 S001041 JAMISON & CLA | 2028 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312114 | REP WEST CM22 NP_2 S001041 JAMISON & CLA | 2028 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312115 | REP WEST CM22 NP_3 S001041 JAMISON & CLA | 2028 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312119 | REP WEST CM22 NP_1 S001008 YORK & KING S | 2028 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312120 | REP WEST CM22 NP_2 S001008 YORK & KING S | 2028 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261417 | REP CBDTX_T3 S000836 Sony House Druitt | 2025 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261419 | REP CBDTX_T2 S000979 Elizabeth & King St | 2025 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261422 | REP CBDTX_T1 S000979 Elizabeth & King St | 2025 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261425 | REP CBDTX_T3 S000979 Elizabeth & King St | 2025 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261428 | REP CBDTX_T3 S001022 Goulburn & Elizabet | 2025 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261429 | REP CBDTX_T1 S001022 Goulburn & Elizabet | 2026 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261430 | REP CBDTX_T2 S001022 Goulburn & Elizabet | 2026 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261431 | REP CBDTX_T1 S001903 James Hardie Albert | 2026 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261434 | REP CBDTX_T2 S001036 King St Sydney Arca | 2026 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261435 | REP CBDTX_T2 S001020 Kent & Market Sts | 2026 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261436 | REP CBDTX_T3 S001020 Kent & Market Sts | 2026 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261437 | REP CBDTX_T2 S001903 James Hardie Albert | 2027 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261438 | REP CBDTX_T3 S001036 King St Sydney Arca | 2027 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261439 | REP CBDTX_T2 S001019 O'connell St Brook | 2027 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261440 | REP CBDTX_T3 S001019 O'connell St Brook | 2027 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261441 | REP CBDTX_T1 S001036 King St Sydney Arca | 2027 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700270956 | REP CBDTX_1 T0002927 S000547 ROCKWALL CR | 2027 | POTTS POINT | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700270957 | REP CBDTX_2 T0003012 S000547 ROCKWALL CR | 2028 | POTTS POINT | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700270958 | REP CBDTX_3 T0002993 S000547 ROCKWALL CR | 2028 | POTTS POINT | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261452 | REP CBDTX_T1 S000842 Castlereagh & Park | 2028 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261453 | REP CBDTX_T2 S000842 Castlereagh & Park | 2028 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261454 | REP CBDTX_T1 S000836 Sony House Druitt | 2028 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261456 | REP CBDTX_T2 S000836 Sony House Druitt | 2028 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures.
REP_01.03.13 | Bass & Saunders Isolation & Earthing Swit | 1700208977 | REP HV B&S I&E - S000428 BRIDGE & GEORGE | 2025 | SYDNEY | The major issue with these assets relates to operating restrictions associated with the condition of the asset. The switch is not spring assisted and results in WH&S issues for network operators. Moreover, since their switching capacity cannot be determined, incoming feeders must be de-energised to operate the switch, which increases the time and cost of network switching. Projects have been identified based on a condition assessment. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.13 | Bass & Saunders Isolation & Earthing Swit | 1700208978 | REP HV B&S I&E - S000430 BATHURST & KENT | 2025 | SYDNEY | The major issue with these assets relates to operating restrictions associated with the condition of the asset. The switch is not spring assisted and results in WH&S issues for network operators. Moreover, since their switching capacity cannot be determined, incoming feeders must be de-energised to operate the switch, which increases the time and cost of network switching. Projects have been identified based on a condition assessment. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.13 | Bass & Saunders Isolation & Earthing Swit | 1700208991 | REP HV B&S I&E - S000836 SONY HOUSE DRUI | 2026 | SYDNEY | The major issue with these assets relates to operating restrictions associated with the condition of the asset. The switch is not spring assisted and results in WH&S issues for network operators. Moreover, since their switching capacity cannot be determined, incoming feeders must be de-energised to operate the switch, which increases the time and cost of network switching. Projects have been identified based on a condition assessment. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.13 | Bass & Saunders Isolation & Earthing Swit | 1700208992 | REP HV B&S I&E - S000840 PITT ST STRAND | 2026 | SYDNEY | The major issue with these assets relates to operating restrictions associated with the condition of the asset. The switch is not spring assisted and results in WH&S issues for network operators. Moreover, since their switching capacity cannot be determined, incoming feeders must be de-energised to operate the switch, which increases the time and cost of network switching. Projects have been identified based on a condition assessment. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.13 | Bass & Saunders Isolation & Earthing Swit | 1700208993 | REP HV B&S I&E - S000841 SUSSEX & GOULBU | 2027 | SYDNEY | The major issue with these assets relates to operating restrictions associated with the condition of the asset. The switch is not spring assisted and results in WH&S issues for network operators. Moreover, since their switching capacity cannot be determined, incoming feeders must be de-energised to operate the switch, which increases the time and cost of network switching. Projects have been identified based on a condition assessment. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.13 | Bass & Saunders Isolation & Earthing Swit | 1700208994 | REP HV B&S I&E - S000842 CASTLEREAGH & P | 2027 | SYDNEY | The major issue with these assets relates to operating restrictions associated with the condition of the asset. The switch is not spring assisted and results in WH&S issues for network operators. Moreover, since their switching capacity cannot be determined, incoming feeders must be de-energised to operate the switch, which increases the time and cost of network switching. Projects have been identified based on a condition assessment. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.13 | Bass & Saunders Isolation & Earthing Swit | 1700209000 | REP HV B&S I&E - S000856 PITT & HUNTER S | 2028 | SYDNEY | The major issue with these assets relates to operating restrictions associated with the condition of the asset. The switch is not spring assisted and results in WH&S issues for network operators. Moreover, since their switching capacity cannot be determined, incoming feeders must be de-energised to operate the switch, which increases the time and cost of network switching. Projects have been identified based on a condition assessment. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.13 | Bass & Saunders Isolation & Earthing Swit | 1700209001 | REP HV B&S I&E - S000863 MACQUARIE ST MA | 2028 | SYDNEY | The major issue with these assets relates to operating restrictions associated with the condition of the asset. The switch is not spring assisted and results in WH&S issues for network operators. Moreover, since their switching capacity cannot be determined, incoming feeders must be de-energised to operate the switch, which increases the time and cost of network switching. Projects have been identified based on a condition assessment.
REP_02.02.46 | SCADA Schemes - ZN & TS | 1700438527 | REP SCADA SYSTEM TS07150 PYRMONT STS | 2025 | PYRMONT | Ausgrid has numerous unsupported proprietary SCADA systems and components installed in sub-transmission, zone and distribution substations that are now beyond their standard technical life. In all cases the maintenance and support (including replacement parts) has ceased for these legacy systems (those identified for replacement) as the hardware components are no longer available. Ausgrid’s legacy proprietary SCADA equipment also cannot support modern feeder protection relays will not support the enablement of future network capability including the Advanced Distribution Management System (ADMS). Failure of SCADA systems in zones means that visibility and controllability of the zone is lost: in the event of a fault the control room is unable to perform switching to restore supply. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_02.02.46 | SCADA Schemes - ZN & TS | 1700438534 | REP SCADA SYSTEM ZN04990 CITY CENTRAL | 2025 | SYDNEY | Ausgrid has numerous unsupported proprietary SCADA systems and components installed in sub-transmission, zone and distribution substations that are now beyond their standard technical life. In all cases the maintenance and support (including replacement parts) has ceased for these legacy systems (those identified for replacement) as the hardware components are no longer available. Ausgrid’s legacy proprietary SCADA equipment also cannot support modern feeder protection relays will not support the enablement of future network capability including the Advanced Distribution Management System (ADMS). Failure of SCADA systems in zones means that visibility and controllability of the zone is lost: in the event of a fault the control room is unable to perform switching to restore supply. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_02.02.46 | SCADA Schemes - ZN & TS | 1700501072 | REP SCADA SYSTEM TS07140 BUNNERONG NORTH | 2026 | MATRAVILLE | Ausgrid has numerous unsupported proprietary SCADA systems and components installed in sub-transmission, zone and distribution substations that are now beyond their standard technical life. In all cases the maintenance and support (including replacement parts) has ceased for these legacy systems (those identified for replacement) as the hardware components are no longer available. Ausgrid’s legacy proprietary SCADA equipment also cannot support modern feeder protection relays will not support the enablement of future network capability including the Advanced Distribution Management System (ADMS). Failure of SCADA systems in zones means that visibility and controllability of the zone is lost: in the event of a fault the control room is unable to perform switching to restore supply. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_02.02.46 | SCADA Schemes - ZN & TS | 1700660569 | REP SCADA SYSTEM ZN09550 GWAWLEY BAY | 2027 | MIRANDA | Ausgrid has numerous unsupported proprietary SCADA systems and components installed in sub-transmission, zone and distribution substations that are now beyond their standard technical life. In all cases the maintenance and support (including replacement parts) has ceased for these legacy systems (those identified for replacement) as the hardware components are no longer available. Ausgrid’s legacy proprietary SCADA equipment also cannot support modern feeder protection relays will not support the enablement of future network capability including the Advanced Distribution Management System (ADMS). Failure of SCADA systems in zones means that visibility and controllability of the zone is lost: in the event of a fault the control room is unable to perform switching to restore supply. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_02.02.46 | SCADA Schemes - ZN & TS | 1700438532 | REP SCADA SYSTEM ZN07481 DARLING HARBOUR | 2028 | PYRMONT | Ausgrid has numerous unsupported proprietary SCADA systems and components installed in sub-transmission, zone and distribution substations that are now beyond their standard technical life. In all cases the maintenance and support (including replacement parts) has ceased for these legacy systems (those identified for replacement) as the hardware components are no longer available. Ausgrid’s legacy proprietary SCADA equipment also cannot support modern feeder protection relays will not support the enablement of future network capability including the Advanced Distribution Management System (ADMS). Failure of SCADA systems in zones means that visibility and controllability of the zone is lost: in the event of a fault the control room is unable to perform switching to restore supply. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_02.02.59 | Neutral Earthing Resistors - ZN & TS | 1700374868 | REP NER X3 TS07220 WILLOUGHBY | 2025 | ARTARMON | These are approaching end of life and have hidden failure modes. Failure of these assets delays fault clearing and reduces the life of related switchgear. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_02.02.59 | Neutral Earthing Resistors - ZN & TS | 1700374870 | REP NER R1 TS00402 ERARING | 2025 | ERARING | These are approaching end of life and have hidden failure modes. Failure of these assets delays fault clearing and reduces the life of related switchgear. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_02.02.59 | Neutral Earthing Resistors - ZN & TS | 1700756324 | REP NER R2 TS00402 ERARING | 2026 | ERARING | These are approaching end of life and have hidden failure modes. Failure of these assets delays fault clearing and reduces the life of related switchgear.
REP_04.02.01 | Steel Mains (km) | 1700475909 | REP 6797m STLM_35197 ZN00515 MT THORLEY | 2027 | GARLAND VALLEY | Protective galvanised coating of the steel mains and conductor ties degrades with age and can pose environmental risks, such as fires, public safety and failure of supply. Replacement of the steel mains are identified using an condition assessment process that used inspection, spatial risk factors and failure data. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700214276 | REP 226m CONSAC HS24852 SOUTH SEAS DRIVE | 2025 | ASHTONFIELD | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700214317 | REP 393m CONSAC HS54095_24922 GREENHILLS | 2025 | EAST MAITLAND | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700214251 | REP 170m CONSAC HP46037_46037 ABERGLASSL | 2025 | RUTHERFORD | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700214255 | REP 302m CONSAC HP52319_52319 OMARU | 2025 | CESSNOCK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700214250 | REP 184m CONSAC HP01685_1685 MAITLAND RD | 2025 | BOLWARRA | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200463 | REP 201m CONSAC S002808_2 SURREY ST S W | 2025 | EPPING | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200465 | REP 446m CONSAC S001719_1 BRIGHTON BLVD | 2025 | NORTH BONDI | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200467 | REP 481m CONSAC S004221_3 HELEN STREET W | 2025 | LANE COVE NORTH | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200681 | REP 640m CONSAC S035893_2 CRANBROOK ROAD | 2025 | ROSE BAY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200697 | REP 614m CONSAC S006125_1 SHEPHERDS DR & | 2025 | CHERRYBROOK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200702 | REP 626m CONSAC S005447_2 PARKHILL CRES | 2025 | CHERRYBROOK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700501188 | REP 413m CONSAC S006013_3 KHARTOUM RD E | 2025 | MACQUARIE PARK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200705 | REP 581m CONSAC S004020_2 ALVONA AVE E | 2025 | ST IVES | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200710 | REP 205m CONSAC S004944_2 CRAIGLANDS AV | 2025 | GORDON | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200716 | REP 399m CONSAC S001796_2 HERRING RD WS | 2025 | MARSFIELD | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200722 | REP 442m CONSAC S005345_1 FRANCIS GREEN | 2025 | CHERRYBROOK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200723 | REP 526m CONSAC S005570_1 FRANCIS GREEN | 2025 | CHERRYBROOK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700488351 | REP 172m CONSAC S005768_2 SHEPHERDS DR | 2025 | CHERRYBROOK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200743 | REP 186m CONSAC S002690_3 BOTANY RD EAST | 2025 | BANKSMEADOW | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200744 | REP 189m CONSAC S036083_3 WALLEROY RD NT | 2025 | WOOLLAHRA | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200746 | REP 157m CONSAC S005288_1 AVENUE RD. W/N | 2025 | MOSMAN | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200753 | REP 544m CONSAC S005288_2 AVENUE RD W/N | 2025 | MOSMAN | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200754 | REP 566m CONSAC S009675_3 JAMES COOK IS | 2025 | SYLVANIA WATERS | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200756 | REP 431m CONSAC S005189_2 SHIPWAY ST E | 2025 | MARSFIELD | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200758 | REP 130m CONSAC S005036_1 HINEMOA ST & 1 | 2025 | PANANIA | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200765 | REP 137m CONSAC S009872_2 TURRIELL PT R | 2025 | PORT HACKING | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200769 | REP 498m CONSAC S000027_1 S8164,S4104&LY | 2026 | MACQUARIE PARK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200771 | REP 210m CONSAC S003799_3 OXFORD ST E N | 2026 | EPPING | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200772 | REP 353m CONSAC S001719_2 RAMSGATE AVE U | 2026 | NORTH BONDI | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200775 | REP 179m CONSAC S002664_3 CUMBERLAND RD | 2026 | AUBURN | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200778 | REP 290m CONSAC S003800_1 CAMBRIDGE ST | 2026 | EPPING | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200780 | REP 312m CONSAC S004221_1 HELEN STREET E | 2026 | LANE COVE NORTH | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200781 | REP 171m CONSAC S003167_4 CAMERON ST OH | 2026 | EDGECLIFF | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200788 | REP 222m CONSAC S005905_3 MARRICKVILLE R | 2026 | MARRICKVILLE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200789 | REP 261m CONSAC S001871_1 BALFOUR RD E/N | 2026 | BELLEVUE HILL | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200790 | REP 175m CONSAC S001553_3 VICTORIA ST U | 2026 | ASHFIELD | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200797 | REP 210m CONSAC S004543_2 CHISWICK RD U | 2026 | GREENACRE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200799 | REP 208m CONSAC S004241_2 HEYDON ST _ PA | 2026 | WARRAWEE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200800 | REP 180m CONSAC S004134_3 MILPERRA RD WE | 2026 | REVESBY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200801 | REP 271m CONSAC S002347_3 COORABAN RD | 2026 | MILPERRA | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200802 | REP 212m CONSAC S001234_4 HOWARD RD | 2026 | PADSTOW | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200803 | REP 211m CONSAC S009780_2 OMARU AVE | 2026 | GYMEA | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200804 | REP 279m CONSAC S005046_1 VIRGINIUS ST | 2026 | PADSTOW | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200805 | REP 223m CONSAC S002347_2 WOORANG ST & | 2026 | MILPERRA | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200806 | REP 340m CONSAC S002324_6 MOONBIE ST | 2026 | SUMMER HILL | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200807 | REP 283m CONSAC S000354_1 BLAIR ST UG & | 2026 | BONDI BEACH | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200808 | REP 138m CONSAC S002595_3 WISBEACH ST E | 2026 | ROZELLE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200810 | REP 145m CONSAC S001563_3 MOODIE ST | 2026 | ROZELLE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200813 | REP 191m CONSAC S009770_2 BURKE RD N W & | 2026 | CRONULLA | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200816 | REP 598m CONSAC S004279_3 WAIROA AVE UG | 2026 | BONDI | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200819 | REP 948m CONSAC S003954_2 MARCEAU DR SO | 2026 | CONCORD | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200820 | REP 309m CONSAC S004903_1 GANMAIN RD UG | 2026 | PYMBLE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200821 | REP 285m CONSAC S005065_2 WILGA PLACE O | 2026 | MARSFIELD | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200822 | REP 274m CONSAC S005582_2 CEDARWOOD DRI | 2026 | CHERRYBROOK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200826 | REP 136m CONSAC S005257_2 MODERN AV | 2026 | CANTERBURY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200827 | REP 137m CONSAC S005565_1 MONTAGUE ST | 2026 | BALMAIN | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200829 | REP 138m CONSAC S000169_8 CHARLECOT ST | 2026 | MARRICKVILLE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200836 | REP 185m CONSAC S001880_1 SHARPE ST & S | 2027 | BELMORE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700495802 | REP 350m CONSAC S006012_4 MILITARY RD | 2027 | MOSMAN | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200840 | REP 611m CONSAC S005769_1 WISTERIA CR S | 2027 | CHERRYBROOK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200843 | REP 100m CONSAC S036083_1 WALLEROY RD NE | 2027 | WOOLLAHRA | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200847 | REP 235m CONSAC S003149_2 THE BOULEVARD | 2027 | DULWICH HILL | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200848 | REP 236m CONSAC S002324_2 LUSTRE DRY CL | 2027 | SUMMER HILL | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200849 | REP 337m CONSAC S009675_2 JAMES COOK IS | 2027 | SYLVANIA WATERS | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200850 | REP 211m CONSAC S077772_3 ADA AVE | 2027 | WAHROONGA | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200851 | REP 287m CONSAC S001853_2 HERRING RD UG | 2027 | MACQUARIE PARK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200852 | REP 218m CONSAC S003685_4 RAWSON ST EAS | 2027 | AUBURN | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200853 | REP 133m CONSAC S001753_4 O'CONNELL ST N | 2027 | NEWTOWN | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200857 | REP 126m CONSAC S003361_3 CHALEYER ST W | 2027 | ROSE BAY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700200863 | REP 292m CONSAC S001681_3 WARATAH STREET | 2027 | RUSHCUTTERS BAY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200865 | REP 443m CONSAC S007971_2 WELLINGTON ST | 2027 | BONDI BEACH | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200866 | REP 544m CONSAC S000354_5 MITCHELL ST W | 2027 | BONDI BEACH | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200868 | REP 227m CONSAC S005568_2 MACQUARIE DR | 2027 | CHERRYBROOK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200870 | REP 296m CONSAC S005568_1 MACQUARIE DR | 2027 | CHERRYBROOK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200871 | REP 349m CONSAC S005553_1 EDWARD BENNETT | 2027 | CHERRYBROOK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200873 | REP 134m CONSAC S009509_3 ANZAC AVE EAS | 2027 | ENGADINE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200876 | REP 160m CONSAC S005256_3 ROGAL PL W N | 2027 | MACQUARIE PARK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200879 | REP 128m CONSAC S005162_2 MYRA ST | 2027 | WAHROONGA | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200891 | REP 187m CONSAC S004530_1 BOTANY RD UG | 2027 | BOTANY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200892 | REP 172m CONSAC S001222_1 HUME HWY WEST | 2027 | YAGOONA | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200895 | REP 197m CONSAC S000353_6 COUNCIL ST DA | 2027 | BONDI JUNCTION | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200897 | REP 422m CONSAC S005928_1 COLLEEN CRES | 2027 | CHERRYBROOK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200898 | REP 425m CONSAC S005469_2 CEDARWOOD DR U | 2027 | CHERRYBROOK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200900 | REP 240m CONSAC S002648_3 SEBASTAPOL ST | 2027 | MARRICKVILLE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200901 | REP 292m CONSAC S000382_2 ADDERLEY ST W | 2027 | AUBURN | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200902 | REP 164m CONSAC S003954_3 MARCEAU DR WE | 2027 | CONCORD | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200904 | REP 200m CONSAC S007562_2 Ridge St South | 2027 | GORDON | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200905 | REP 208m CONSAC S004910_2 CARBEEN AVE | 2028 | ST IVES | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200906 | REP 240m CONSAC S005064_2 CLOVELLY RD S | 2028 | HORNSBY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200911 | REP 168m CONSAC S003671_1 COLLEGE ST | 2028 | CROYDON | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200912 | REP 172m CONSAC S003001_2 CHESTER HILL R | 2028 | CHESTER HILL | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200928 | REP 139m CONSAC S009874_3 CRESCENT RD EA | 2028 | CARINGBAH | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200935 | REP 151m CONSAC S002550_3 WATSON ST NORT | 2028 | BONDI | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200936 | REP 148m CONSAC S005472_2 MALABAR RD NOR | 2028 | SOUTH COOGEE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200939 | REP 154m CONSAC S001709_1 767_771 PACIFI | 2028 | GORDON | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700200940 | REP 137m CONSAC S001922_2 RAWSON ST | 2028 | LIDCOMBE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700200942 | REP 419m CONSAC S002765_3 MILITARY RD UG | 2028 | MOSMAN | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700200943 | REP 849m CONSAC S003459_2 CHILDS ST U G | 2028 | LIDCOMBE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700200944 | REP 621m CONSAC S004020_1 ALVONA AVE W | 2028 | ST IVES | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700200945 | REP 635m CONSAC S002381_3 GLEN AYR AVE | 2028 | BONDI BEACH | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700200954 | REP 192m CONSAC S001716_3 OLD SOUTH HEAD | 2028 | BELLEVUE HILL | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700200955 | REP 460m CONSAC S005321_1 MORRIS AVE UG | 2028 | THORNLEIGH | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700200956 | REP 519m CONSAC S009811_2 TEA TREE PL N | 2028 | KIRRAWEE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700200957 | REP 474m CONSAC S003701_4 EPPING RD UG | 2028 | DOUBLE BAY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700200958 | REP 436m CONSAC S005447_1 PARKHILL CRES | 2028 | CHERRYBROOK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700200960 | REP 267m CONSAC S004893_2 ROBINSON ST W | 2028 | EAST LINDFIELD | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700200961 | REP 272m CONSAC S000549_1 NO71 PRINCES H | 2028 | ST PETERS | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700200962 | REP 204m CONSAC S004433_2 BAY ROAD | 2028 | WAVERTON | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700200963 | REP 245m CONSAC S004719_1 BERILDA AVE | 2028 | WARRAWEE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700200965 | REP 251m CONSAC S004954_2 DAVIES RD | 2028 | PADSTOW | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700200966 | REP 210m CONSAC S004425_1 HOPE ST | 2028 | PYMBLE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700200968 | REP 207m CONSAC S004142_3 LINDEN AVE | 2028 | PYMBLE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700200969 | REP 170m CONSAC S002734_1 JOSEPH ST NORT | 2028 | LIDCOMBE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.06 | Low Voltage HDPE Cables (km) | 1700245584 | REP 182m HDPE S001191_1 NO11 CHURCHILL S | 2025 | SILVERWATER | Ausgrid has approximately 110km of LV HDPE cable installed on its distribution network, which was installed between the mid 1970s until the mid 1980s. Ausgrid's HDPE LV cables have higher failure rates than other types of LV cable on the network. The need to replace HDPE cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all HDPE cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.06 | Low Voltage HDPE Cables (km) | 1700394845 | REP 96m HDPE S001986_3 ALBERT ST W OH OC | 2026 | EDGECLIFF | Ausgrid has approximately 110km of LV HDPE cable installed on its distribution network, which was installed between the mid 1970s until the mid 1980s. Ausgrid's HDPE LV cables have higher failure rates than other types of LV cable on the network. The need to replace HDPE cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all HDPE cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | No Change
REP_04.02.12 | LV Metallic Sheathed Cables (km) | 1700520064 | REP 171m Met Sheath Cable S003750_5 King | 2025 | SYDNEY | Ausgrid has approximately 785km of Low Voltage underground metallic sheathed cable which supply electricity from distribution substations to customers. LV metallic sheathed cable failures can result in consequences including safety risks, fire risk, unserved energy and other risks. A planned replacement strategy has been adopted for the replacement of LV metallic sheathed cable based on a detailed risk assessment. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.12 | LV Metallic Sheathed Cables (km) | 1700520067 | REP 196m Met Sheath Cable S006703_4 Fitz | 2025 | MARRICKVILLE | Ausgrid has approximately 785km of Low Voltage underground metallic sheathed cable which supply electricity from distribution substations to customers. LV metallic sheathed cable failures can result in consequences including safety risks, fire risk, unserved energy and other risks. A planned replacement strategy has been adopted for the replacement of LV metallic sheathed cable based on a detailed risk assessment. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.12 | LV Metallic Sheathed Cables (km) | 1700520114 | REP 201m Met Sheath Cable S000224_3 Henr | 2026 | ULTIMO | Ausgrid has approximately 785km of Low Voltage underground metallic sheathed cable which supply electricity from distribution substations to customers. LV metallic sheathed cable failures can result in consequences including safety risks, fire risk, unserved energy and other risks. A planned replacement strategy has been adopted for the replacement of LV metallic sheathed cable based on a detailed risk assessment. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700681449 | TRANSMISSION FEEDER & TOWER RECOVERY | 2025 | Homebush | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700354217 | REP TOWER 25C LE35910 FDR 910/911 | 2025 | CANTERBURY | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700795506 | REP TOWER FF00511 9M1-9M2-043 | 2025 | FRENCHS FOREST | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option.
REP_05.02.01-5 | Tower Replacement | 1700330814 | REP DS4 TOWER 04 PE25151 FDR 910/911 | 2025 | REVESBY HEIGHTS | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2025 | No Change
REP_05.02.01-5 | Tower Replacement | 1700330815 | REP DS4 TOWER 06 PE25153 FDR 910/911 | 2026 | PADSTOW HEIGHTS | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700330819 | REP DS4 TOWER 02 PE25149 FDR 910/911 | 2026 | PICNIC POINT | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700379143 | REP TOWER 952-001 FDR 95A | 2026 | KILLINGWORTH | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700440038 | REP TWR REPLACEMENT PRIORITY DESIGN | 2026 | Homebush | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2026 | No Change
REP_05.02.01-5 | Tower Replacement | 1700550482 | REP COMMS TOWER STRUCTURAL Black mntn | 2026 | Wingen | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2026 | No Change
REP_05.02.01-5 | Tower Replacement | 1700642438 | REP TOWER KL488 FDR 916/917 | 2027 | KURNELL | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700642435 | REP TOWER KL487 FDR 916/917 | 2027 | KURNELL | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700642422 | REP TOWER KL486 FDR 916/917 | 2027 | KURNELL | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700642416 | REP TOWER KL485 FDR 916/917 | 2027 | KURNELL | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700642436 | REP TOWER KL484 FDR 916/917 | 2027 | KURNELL | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700642425 | REP TOWER KL489 FDR 916/917 | 2028 | KURNELL | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700642433 | REP TOWER CR9147 FDR 916/917 | 2028 | KURNELL | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700642440 | REP TOWER CR9148 FDR 916/917 | 2028 | KURNELL | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700642443 | REP TOWER CR9145 FDR 916/917 | 2028 | KURNELL | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2023 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700642442 | REP TOWER CR9144 FDR 916/917 | 2028 | KURNELL | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.