## Below 200k
REG_ID | Reg Name | Time | Areas | Planning methodology | Proposed time in 2024 DTAPR | Reason for change
DOC_11.03.38 | Optical Arc Fault Protection | 2025,2026,2027,2028,2029, | Homebush,OATLEY,SYDCBD,Sydney Northeast,Sydney Northwest, | The optical arc fault protection program is driven by the need to protect the safety of workers so far as is reasonably practicable at substations. The present summated current protection schemes are inadequate and will be replaced with the modern standard optical arc fault protection systems. The modern optical arc fault protection systems will also operate to limit the damage to other network assets. | 2024,2025,2026,2027,2028, | No Change
DOC_11.03.54 | Asbestos Fire Doors - ZN & TS | 2026,2027,2028,2029, | Newcastle ,SYDCBD, | The primary function of a fire door is to prevent the spread of fire. Asbestos contained within these fire doors is a safety risk to workers and the public. Ausgrid has a duty of care to eliminate or where this is not practicable minimise safety risks to as low as is reasonably practicable. | 2024,2025,2026,2027,2028, | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.69 | Siemens 8DN8 Circuitry Modification - ZN | 2026,2027,2028,2029, | Homebush,Newcastle ,Ourimbah,SYDCBD,Sydney Northeast, | The Siemens 8DN8 low gas alarm circuitry renewal is driven by the National Electricity Rules compliance that prevents a single point of failure that would cause both primary and backup protection to fail. The present configuration does not meet this requirement as the failure of the low gas alarm sensor can inhibit the operation of the primary and back-up protection systems. Renewal of the circuitry will eliminate this failure mode. | 2024,2025,2026,2027,2028, | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 2025,2026,2027,2028,2029, | Homebush,Lower Hunter ,Newcastle ,OATLEY,Ourimbah,SYDCBD,Sydney Northeast,Sydney Northwest | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024,2025,2026,2027,2028, | No Change
DOC_11.03.77 | Substation Locks Upgrade | 2026, | Homebush,Newcastle ,SYDCBD, | Ausgrid has a duty of care to the public and its workers by limiting access to hazardous electrical equipment. Substations contain hazardous electrical equipment that has the potential to harm the public. Unauthorised access with the intent to harm and disrupt is also considered as a possibility. This program will improve the security of Ausgrid's substations. | 2025,2026, | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.02 | A,B & C Type Kiosks | 2025,2026,2027,2028,2029, | Homebush,SYDCBD,Sydney Northeast,Sydney Northwest,Upper Hunter , | The ABC type kiosk are the oldest kiosk on Ausgrid's network, are of an obsolete design and are in a poor condition. Projects are identified and prioritised for replacement based on an asset condition risk assessment. | 2024,2025,2026,2027,2028, | No Change
REP_01.02.42 | Outdoor Enclosure Substations | 2025,2026,2027,2028,2029, | Homebush,OATLEY,SYDCBD,Sydney Northeast,Sydney Northwest, | The Outdoor Enclosure (OE) type distribution substations are substation design which is no longer approved. OE substations that are approaching end of life may require multiple individual components to be replaced, making it more cost effective to replace the OE substations. | 2024,2025,2026,2027,2028, | No Change
REP_01.02.43 | HV OCB Subs | 2025,2026,2027,2028,2029, | Homebush,Newcastle ,SYDCBD,Sydney Northeast,Sydney Northwest, | The current population of oil circuit breakers is deteriorating and spare components are becoming difficult to obtain as the equipment is no longer manufactured. This program aligns with Ausgrid’s strategy of progressively removing oil filled switchgear. A detailed condition risk assessment was conducted and a prioritised planned replacement program was developed to mitigate the associated risk. | 2024,2025,2026,2027,2028, | No Change
REP_01.02.45 | Statter_ALM_Godfrey HV Fuse Switches | 2026,2027,2028,2029, | Homebush,OATLEY,Ourimbah,SYDCBD,Sydney Northeast,Sydney Northwest, | These HV fuse switches are being replaced due to increasing number of failures and limited availability of spares as well as technical support being no longer available. Majority of the switches are oil filled and failures can pose serious public safety risks if a fire follows the failure. | 2024,2025,2026,2027,2028, | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.47 | Reyrolle JKSS RMIs C_EB | 2026, | Homebush,SYDCBD, | The Reyrolle JKSS RMIs have a range of safety and operational issues and they are approach their end of life. These assets are experiencing a range of asset condition issues including oil leaks from the main tank and corrosion of support structure and main body. Projects within this program are identified based on an asset condition risk assessment. | 2024,2025,2026, | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.52 | Obsolete RMIs & FSs | 2025,2026,2027,2028,2029, | Homebush,Lower Hunter ,Newcastle ,OATLEY,Ourimbah,SYDCBD,Sydney Northeast,Sydney Northwest | This program funds the replacement of 11kV Ring Main Isolators (RMIs) & Fuse Switches (FS) that have been approach their end of life. Projects within this program are identified based on an asset condition risk assessment.. | 2024,2025,2026,2027,2028, | No Change
REP_01.02.57 | ABB 11kV Series V EDO Fuse Carriers | 2025, | Homebush,Lower Hunter ,Newcastle ,OATLEY,Ourimbah,Sydney Northeast,Sydney Northwest,Upper Hunter | There have been a number of failures associated with ABB Series V 11kV EDO Fuse Carriers used on Pole Top transformer (PT) substations, resulting in customer interruptions and leading to safety and operational concerns for Ausgrid staff and the public. The program is driven by inherent design issues with the construction rather than condition or age. | 2024,2025, | No Change
REP_01.02.59 | SCADA Equipment - DC | 2026,2027,2028,2029, | SYDCBD, | The SCADA equipment in Sydney CBD distribution centres were installed in early 1990s is now approaching end of life and is increasingly difficult to maintain. | 2025,2026,2027,2028, | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.04 | Single Circuit Breaker Switchgear | 2026,2027,2028, | SYDCBD, | The current population of breakers at single circuit breaker substations are deteriorating. Most of them were commissioned during the 1960s and there are ongoing issues associated with these breakers including oil leaks and difficulties with the operating mechanism. These breakers also utilise copper pilot cables for disconnecting faults and these cables have high failure rates as they are of a similar age to the substation equipment. Locating and repairing defects on these underground communications cables is expensive due to the need to excavate roads to access the cable for repair. Ausgrid has conducted a detailed condition risk assessment of these assets and developed a prioritised planned replacement program to mitigate the risk associated with these assets. | 2024,2025,2026,2027,2028, | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.16 | Muswellbrook Kiosks | 2026,2027,2028,2029, | Upper Hunter , | These kiosk substations are approaching their end of life and require replacement. There are a range of asset condition, operational and safety issues associated with this type of substation. Additionally, certain replacement parts for this type of substation are unable to be procured. Projects within this program are identified based on an asset condition risk assessment... | 2024,2025,2026,2027,2028, | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.17 | Hazemeyer RMIs - Harsh Environment | 2026,2027,2028,2029, | Homebush,OATLEY,SYDCBD,Sydney Northeast, | The replacement program for Hazemeyer ring main units in harsh environments was initiated following a review of condition of this class of asset. Environmental factors, such as high pollution and salt spray in coastal areas, have affected the condition of these assets. Projects within this program are identified and prioritised based on an asset condition risk assessment. | 2024,2025,2026,2027,2028, | Work has been reprioritised based on condition and risk assessment and available resources.
REP_02.02.09 | Earthing system - ZN | 2025,2026,2027,2028, | Lower Hunter ,Newcastle ,OATLEY,Ourimbah,SYDCBD,Sydney Northeast,Sydney Northwest,Upper Hunter , | The major substation earthing system is to protect people and the asset as well as endsuring exposed equipment is safe to touch during normal operation. This program funds the replacement of earthing equipment within zone substations and subtransmission substations. | 2024,2025,2026,2027, | Work has been reprioritised based on condition and risk assessment and available resources.
REP_02.02.38 | 33KV I&Es - ZN & TS | 2025,2026,2027,2028,2029, | Homebush,Newcastle ,OATLEY,Ourimbah,Sydney Northeast,Sydney Northwest,Upper Hunter , | The 33kV Non-Essantee isolator switches have a history of failures which have impacted reliability of the network and the safety of workers. Failure modes include: .• Welded primary contacts, or overheating primary contacts;.• Corrosion of support steel work;.• Security/integrity of earth bar connections and crimps;.• Damaged support insulators..Such failures have potential to cause safety and operation issues. Projects within this program are identified and prioritised based on an asset condition risk assessment.. | 2024,2025,2026,2027,2028, | No Change
REP_02.02.60 | 11kV Switchboard Protection - ZN & TS | 2026, | Homebush,SYDCBD,Sydney Northeast, | A significant portion of Ausgrid's 11kV Switchgear protection scheme relays utilise electromechanical technology. These assets have hidden failure modes which mean that failures are not detected until it is required to operate. Many of these older relays are no longer supported by manufacturers and spare parts are not available and replacement involves new technology which takes additional time to install. The program funds the replacement of 11kV busbar protection schemes at end-of-life which extends the effective life of the switchboard. | 2024,2025,2026, | Work has been reprioritised based on condition and risk assessment and available resources.
REP_02.02.62 | SCADA Equipment - ZN & TS | 2025,2026,2027,2028,2029, | Homebush,Newcastle ,OATLEY,Ourimbah,SYDCBD,Sydney Northeast,Sydney Northwest,Upper Hunter | The SCADA equipment in Sydney CBD zone substations have conditional and aging issues. Considering the high reliability requirement in the CBD area, they are recommended to be replaced. | 2024,2025,2026,2027,2028, | No Change
REP_02.03.05 | 132/66kV Bushings - ZN & TS | 2025,2026, | Homebush,Ourimbah,SYDCBD,Sydney Northwest,Upper Hunter , | Oil Impregnated Paper transformer bushings poses risk of explosive failure, which represent a safety hazard and can cause excessive damage to substation equipment. Following the catastrophic failure of several oil impregnated paper bushings on Ausgrid’s network, investigations were carried out into the condition of these assets. The investigations found that there was a degradation of the insulation material resulting in water ingress in the bushing. The seriousness of bushing failures instigated a proactive replacement program of this type of oil impregnated paper bushings. The bushing replacement programs form part of Ausgrid’s strategy to meet its obligations to manage the risks of these assets failing so far as is reasonably practicable. | 2024,2025,2026, | No Change
REP_02.03.07 | Protection Relays - ZN & TS | 2025,2026,2027, | Newcastle ,SYDCBD,Sydney Northeast,Sydney Northwest, | This program is to replace the protection relays that are in poor condition. Failure of protection relays put primary assets at risk and can lead to safety incidnts, property damage and loss of supply. Projects are identified using a condition assessment process. | 2024,2025,2026,2027,., | No Change
REP_02.03.08 | High Priority Relays - ZN & TS | 2026,2027,2028, | Homebush,Newcastle ,Ourimbah,SYDCBD, | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, these relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. | 2025,2026, | Work has been reprioritised based on condition and risk assessment and available resources.
REP_02.03.11 | Batteries and Battery Charging Equipment | 2026,2027,2028,2029, | Homebush,Newcastle ,OATLEY,SYDCBD,Sydney Northeast,Upper Hunter , | Failure of the battery scheme whilst the substation is energised can result in the loss of power to the substation’s electrical protection systems. The dominant failure mode of batteries is the loss of capacity due to an internal fault of the cell, which is a nonrepairable failure mode and requires replacement to ensure the battery meets substation performance requirements. ..Batteries that have degraded are unable to hold charge and will not operate when required. The degradation of battery systems means that they need to be replaced to provide the required function. Battery chargers are matched to the battery technology and therefore need to be replaced upon battery technology change to maintain compatibility | 2024,2025,2026,2027,2028, | No Change
REP_04.02.01 | Steel Mains (km) | 2025,2026,2027,2028,2029, | Lower Hunter ,OATLEY,Ourimbah,Sydney Northeast,Sydney Northwest,Upper Hunter , | Protective galvanised coating of the steel mains and conductor ties degrades with age and can pose environmental risks, such as fires, public safety and failure of supply. Replacement of the steel mains are identified using an condition assessment process that used inspection, spatial risk factors and failure data. | 2025,2026,2027, | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 2025,2026,2027,2028,2029, | Homebush,Lower Hunter ,OATLEY,Ourimbah,SYDCBD,Sydney Northeast,Sydney Northwest, | Ausgrid has approximately 785km of Low Voltage underground metallic sheathed cable which supply electricity from distribution substations to customers. LV metallic sheathed cable failures can result in consequences including safety risks, fire risk, unserved energy and other risks. A planned replacement strategy has been adopted for the replacement of LV metallic sheathed cable based on a detailed risk assessment. | 2024,2025,2026,2027,2028, | No Change
REP_04.02.06 | Low Voltage HDPE Cables (km) | 2026,2027,2028,2029, | Homebush,OATLEY,SYDCBD,Sydney Northeast,Sydney Northwest, | Ausgrid has approximately 110km of LV HDPE cable installed on its distribution network, which was installed between the mid 1970s until the mid 1980s. Ausgrid's HDPE LV cables have higher failure rates than other types of LV cable on the network. ..The need to replace HDPE cables has been triggered by condition related issues which have resulted in;.• safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and.• network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. ..Ausgrid has developed a prioritised planned replacement program of all HDPE cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2024,2025,2026,2027,2028, | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.11 | 11kV UGOHs | 2025,2026,2027,2028,2029, | Lower Hunter ,Newcastle ,OATLEY,Ourimbah,Sydney Northeast, | Unlike modern UGOHs which use heat shrink insulation, pot head UGOHs can fail explosively as the cables are terminated inside an oil/compound filled metal casing. The failure of pot head UGOHs is exacerbated by being located in outdoor public areas. Potential hazards include injury to public and staff, live conductors falling to the ground. | 2024,2025,2026,2027,2028, | No Change
REP_04.02.12 | LV Metallic Sheathed Cables (km) | 2025,2026, | SYDCBD, | Low voltage metallic sheathed cable failures can result in consequences such as safety risks, fire risks, unserved energy and other risks. A planned replacement strategy is adopted for the replacement of LV metallic sheathed cable based on a detailed risk assessment of Ausgrid's metallic sheathed cable population. | 2024,2025,2026, | No Change
REP_04.02.36 | 11kV Taplin ABS D571 (No.) | 2026,2027,2028,2029, | Ourimbah,Sydney Northeast, | Air break switches are installed at the top of poles located in public areas. Ausgrid workers stand directly below the air break switches when network switching is undertaken. The need to replace these air break switches has been triggered by a combination of condition and design related issues which have resulted in safety risks to the public, customers and workers due to uncontrolled discharge of electricity or falling components, as well as network reliability risks associated with these failures. Ausgrid workers have experienced ‘near miss’ safety incidents due to failed porcelain insulators falling during network switching and have received electric shocks from poles due to the uncontrolled discharge of electricity from cracked insulators. A functionally failed air break switch is one that has degraded to the point that it is no longer able to be safely operated or has caused a network interruption due to component failure. | 2024,2025,2026,2027,2028, | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.43 | 11kV ABS Haycolec (No.) | 2026, | Sydney Northwest, | Air break switches are installed at the top of poles located in public areas. Ausgrid workers stand directly below the air break switches when network switching is undertaken. The need to replace these air break switches has been triggered by a combination of condition and design related issues which have resulted in safety risks to the public, customers and workers due to uncontrolled discharge of electricity or falling components, as well as network reliability risks associated with these failures. Ausgrid workers have experienced ‘near miss’ safety incidents due to failed porcelain insulators falling during network switching and have received electric shocks from poles due to the uncontrolled discharge of electricity from cracked insulators. A functionally failed air break switch is one that has degraded to the point that it is no longer able to be safely operated or has caused a network interruption due to component failure. | 2024,2025,2026, | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.46 | HV OH Mains (ACSR/Quince) (km) | 2026,2027,2028,2029, | Homebush,Lower Hunter ,Newcastle ,OATLEY,Ourimbah,SYDCBD,Sydney Northeast,Sydney Northwest,Upper Hunter | The protective galvaniing coating of the steel strands in ACSR conductor and conductor ties degrades due to age and environmental factors. This can result in asset failures and pose riks of network fires, public safety and failure of supply. Assets to be replaced are identified using an asset condition assessment process thast used inspection, spatial risk factors and failure data. | 2024,2025,2026,2027,2028, | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.04.01 | LV Overhead Mains - Reactive (km) | 2025,2026,2027, | Homebush,Newcastle ,OATLEY,Ourimbah,SYDCBD,Sydney Northeast,Sydney Northwest,Upper Hunter , | Degradation of overhead conductors and conductor ties can result in fallen conductors which pose risks to public safety and loss of network supply. This program funds the replacement of conditionally failed LV overhead conductor. It is to replace the overhead conductor including the replacements of all conductor phases in any conductor bay or strain section. The scope also includes sections of dedicated LV circuits of bare or PVC insulated construction that must be replaced when dthey are not able to be removed through transferral to LV mains. | 2025,2026, | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.03 | Refurbish Earthing - TM OH Feeders | 2025,2026,2027,2028,2029, | Homebush,Lower Hunter ,Newcastle ,Ourimbah,SYDCBD,Sydney Northeast,Sydney Northwest, | Earthing system on subtransmission feeders is critical for ensuring public and workplace safety, protecting assets and ensuring correct system operation. Deteriorated earthing system will lead to increased electric shock risk as well as equipment failure and increased outages. Ausgrid utilises condition information from inspections / earth resistance testing and condition assessments to determine when an earthing system is approaching functional failure and sets criteria aligned to industry standards to define the point of conditional failure. Earthing systems are replaced or refurbished if the condition issues identified are not technically or economically able to repaired i.e. if they are at end of life. | 2024,2025,2026,2027,2028, | No Change
REP_05.02.12 | Cable Pressure Alarm Replacement | 2025, | SYDCBD, | Cable pressure alarm systems at the end of their serviceable life pose risks such as environmental damage, delay in response time to implement cable repair, increase in breakdown failures. Projects are prioritised based on asset age, likelihood of failure, condition and expected replacement date of the feeder. | 2024, | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.26 | Ground Stays | 2026, | Newcastle , | The replacement of the ground anchors on sub-transmission overhead lines is in response to the number of failures seen in one particular design of ground anchor, primarily used in the upper and lower Hunter and Newcastle regions. Planned projects are identified using a condition assessment process. | 2024, | Work has been reprioritised based on condition and risk assessment and available resources.

## Above 200k
REG_ID | Reg ID Description | Notif # | Notif Desc | Qty | Unit Rate | Notif Cost | Year of Work | Area of work | Planning methodology | Proposed time in 2024 DTAPR | Reason for change
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700264104 | REP CBDTX_T3 S000427 O'connell & Hunter | 1 | 393740.0984 | 393740.0984 | 2025 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures.
REP_04.02.05 | LV Consac Cables (km); | 1700715344 | REP 250m CONSAC HS13269/13274 Cbl Jnt | 1 | 1765426.1973 | 1765426.1973 | 2025 | JEWELLS | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700264103 | REP CBDTX_T1 S000427 O'connell & Hunter | 0.65 | 393740.0984 | 393740.0984 | 2025 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700438043 | REP WEST CM22 NP_3 WILMOT GEORGE - S6198 | 1 | 422597.0516 | 422597.0516 | 2025 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312043 | REP NILSEN NP_1 S000427 O'CONNELL & HUNT | 1 | 422597.0516 | 422597.0516 | 2025 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354313 | DOC LV RECONFIG SLCP264 POLE FF95112 | 8.39 | 33237.7097 | 278864.3845 | 2025 | FRESHWATER | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354379 | DOC LV RECONFIG SLCP666 POLE MA09793 | 6.44 | 33237.7097 | 214050.8506 | 2025 | KINGSFORD | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354383 | DOC LV RECONFIG SLCP669 POLE MA07100 | 11.01 | 33237.7097 | 365947.184 | 2025 | MATRAVILLE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354429 | DOC LV RECONFIG SLCP577 POLE LE03291 | 6.07 | 33237.7097 | 201752.898 | 2025 | DULWICH HILL | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354537 | DOC LV RECONFIG SLCP233 POLE FF87352 | 6.55 | 33237.7097 | 217706.9987 | 2025 | FORESTVILLE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354563 | DOC LV RECONFIG SLCP201 POLE MO84197 | 6.42 | 33237.7097 | 213386.0964 | 2025 | MCMAHONS POINT | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354567 | DOC LV RECONFIG SLCP3608 POLE PE07745 | 6.62 | 33237.7097 | 220033.6383 | 2025 | MORTDALE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354613 | DOC LV RECONFIG SLCP3393 POLE PE13223 | 6.53 | 33237.7097 | 217042.2445 | 2025 | LUGARNO | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354968 | DOC LV RECONFIG SLCP1197 POLE LE02502 | 6.09 | 33237.7097 | 202417.6522 | 2025 | ASHFIELD | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700355143 | DOC LV RECONFIG SLCP3398 POLE PE17783 | 6.43 | 33237.7097 | 213718.4735 | 2025 | HURSTVILLE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700394251 | DOC LV RECONFIG SLCP866 POLE PE10833 | 7.05 | 33237.7097 | 234325.8535 | 2025 | RIVERWOOD | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2028 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700654799 | Remove 621m SL Mains (ex SLCP907) | 7.24 | 33237.7097 | 240641.0184 | 2025 | EAST LINDFIELD | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit.
DOC_11.03.78 | Decommission CBD Vault | 1700208992 | DECOM S000840 PITT ST STRAND | 1 | 731872.6131 | 731872.6131 | 2025 | SYDNEY | Several underground or vault distribution substations located in the Sydney CBD network area are no longer required, with no plans to rebuild a distribution substation on site for the foreseeable future. To prevent these sites from becoming a safety hazard for Ausgrid’s personnel and the public, there is an obligation to disconnect cables, dismantle equipment and remediate the sites. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.78 | Decommission CBD Vault | 1700735415 | DECOM S000431 Elizabeth St St James | 1 | 731872.6131 | 731872.6131 | 2025 | SYDNEY | Several underground or vault distribution substations located in the Sydney CBD network area are no longer required, with no plans to rebuild a distribution substation on site for the foreseeable future. To prevent these sites from becoming a safety hazard for Ausgrid’s personnel and the public, there is an obligation to disconnect cables, dismantle equipment and remediate the sites. | 2025 | No Change
REP_01.02.61 | Intertripping Schemes - DC | 1700438708 | REP 11KV IT PROT S003237 PENNYS LANE | 1 | 232547.173 | 232547.173 | 2025 | POTTS POINT | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.61 | Intertripping Schemes - DC | 1700438716 | REP 11KV IT PROT S003646 WEMYSS WENT | 1 | 232547.173 | 232547.173 | 2025 | SURRY HILLS | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.61 | Intertripping Schemes - DC | 1700438717 | REP 11KV IT PROT S004091 LIVERPOOL NITH | 1 | 232547.173 | 232547.173 | 2025 | SYDNEY | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.61 | Intertripping Schemes - DC | 1700438721 | REP 11KV IT PROT S003692 NIMROD ST | 1 | 232547.173 | 232547.173 | 2025 | DARLINGHURST | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2028 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.61 | Intertripping Schemes - DC | 1700438726 | REP 11KV IT PROT S005051 TELECOM NORTH S | 1 | 232547.173 | 232547.173 | 2025 | NORTH SYDNEY | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700175824 | REP GE OLD NP_1 S003191 AUST CLUB MACQUA | 1 | 422597.0516 | 422597.0516 | 2025 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700283779 | REP WEST CM2 NP_1 S001022 GOULBURN & ELI | 1 | 422597.0516 | 422597.0516 | 2025 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2025 | No Change
REP_01.03.06 | Network Protectors (West CM2/22) | 1700311991 | REP WEST CM2 NP_2 S001022 GOULBURN & ELI | 1 | 422597.0516 | 422597.0516 | 2025 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700311992 | REP WEST CM2 NP_3 S001022 GOULBURN & ELI | 1 | 422597.0516 | 422597.0516 | 2025 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2025 | No Change
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312049 | REP NILSEN NP_1 S000856 PITT & HUNTER ST | 1 | 422597.0516 | 422597.0516 | 2025 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312050 | REP NILSEN NP_2 S000856 PITT & HUNTER ST | 1 | 422597.0516 | 422597.0516 | 2025 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312051 | REP NILSEN NP_3 S000856 PITT & HUNTER ST | 1 | 422597.0516 | 422597.0516 | 2025 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312061 | REP NILSEN NP_1 S000074 NZ LOAN LOFTUS S | 1 | 422597.0516 | 422597.0516 | 2025 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312062 | REP NILSEN NP_2 S000074 NZ LOAN LOFTUS S | 1 | 422597.0516 | 422597.0516 | 2025 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312063 | REP NILSEN NP_3 S000074 NZ LOAN LOFTUS S | 1 | 422597.0516 | 422597.0516 | 2025 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312139 | REP WEST CM22 NP_1 S001173 PITT ST. EMPI | 1 | 422597.0516 | 422597.0516 | 2025 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312140 | REP WEST CM22 NP_2 S001173 PITT ST. EMPI | 1 | 422597.0516 | 422597.0516 | 2025 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312141 | REP WEST CM22 NP_3 S001173 PITT ST. EMPI | 1 | 422597.0516 | 422597.0516 | 2025 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700437953 | REP GE OLD NP_2 S003191 AUST CLUB MACQUA | 1 | 422597.0516 | 422597.0516 | 2025 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700437954 | REP GE OLD NP_3 S003191 AUST CLUB MACQUA | 1 | 422597.0516 | 422597.0516 | 2025 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261428 | REP CBDTX_T3 S001022 Goulburn & Elizabet | 1 | 393740.0984 | 393740.0984 | 2025 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2025 | No Change
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261429 | REP CBDTX_T1 S001022 Goulburn & Elizabet | 1 | 393740.0984 | 393740.0984 | 2025 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261430 | REP CBDTX_T2 S001022 Goulburn & Elizabet | 1 | 393740.0984 | 393740.0984 | 2025 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700264158 | REP CBDTX_T2 S001173 Pitt St. Empire Lan | 1 | 393740.0984 | 393740.0984 | 2025 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700264160 | REP CBDTX_T1 S001173 Pitt St. Empire Lan | 1 | 393740.0984 | 393740.0984 | 2025 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700264161 | REP CBDTX_T3 S001173 Pitt St. Empire Lan | 1 | 393740.0984 | 393740.0984 | 2025 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures.
REP_01.03.13 | Bass & Saunders Isolation & Earthing Swit | 1700209068 | REP HV B&S I&E - S001173 PITT ST. EMPIRE | 1 | 266808.3928 | 266808.3928 | 2025 | SYDNEY | The major issue with these assets relates to operating restrictions associated with the condition of the asset. The switch is not spring assisted and results in WH&S issues for network operators. Moreover, since their switching capacity cannot be determined, incoming feeders must be de-energised to operate the switch, which increases the time and cost of network switching. Projects have been identified based on a condition assessment.
REP_02.02.46 | SCADA Schemes - ZN & TS | 1700438529 | REP SCADA SYSTEM TS00402 ERARING STS | 1 | 431324.2203 | 431324.2203 | 2025 | ERARING | Ausgrid has numerous unsupported proprietary SCADA systems and components installed in sub-transmission, zone and distribution substations that are now beyond their standard technical life. In all cases the maintenance and support (including replacement parts) has ceased for these legacy systems (those identified for replacement) as the hardware components are no longer available. Ausgrid’s legacy proprietary SCADA equipment also cannot support modern feeder protection relays will not support the enablement of future network capability including the Advanced Distribution Management System (ADMS). Failure of SCADA systems in zones means that visibility and controllability of the zone is lost: in the event of a fault the control room is unable to perform switching to restore supply.
REP_02.02.46 | SCADA Schemes - ZN & TS | 1700438532 | REP SCADA SYSTEM ZN07481 DARLING HARBOUR | 1 | 431324.2203 | 431324.2203 | 2025 | PYRMONT | Ausgrid has numerous unsupported proprietary SCADA systems and components installed in sub-transmission, zone and distribution substations that are now beyond their standard technical life. In all cases the maintenance and support (including replacement parts) has ceased for these legacy systems (those identified for replacement) as the hardware components are no longer available. Ausgrid’s legacy proprietary SCADA equipment also cannot support modern feeder protection relays will not support the enablement of future network capability including the Advanced Distribution Management System (ADMS). Failure of SCADA systems in zones means that visibility and controllability of the zone is lost: in the event of a fault the control room is unable to perform switching to restore supply. | 2028 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_02.02.46 | SCADA Schemes - ZN & TS | 1700438612 | REP SCADA SYSTEM TS07170 SURRY HILLS STS | 1 | 431324.2203 | 431324.2203 | 2025 | SURRY HILLS | Ausgrid has numerous unsupported proprietary SCADA systems and components installed in sub-transmission, zone and distribution substations that are now beyond their standard technical life. In all cases the maintenance and support (including replacement parts) has ceased for these legacy systems (those identified for replacement) as the hardware components are no longer available. Ausgrid’s legacy proprietary SCADA equipment also cannot support modern feeder protection relays will not support the enablement of future network capability including the Advanced Distribution Management System (ADMS). Failure of SCADA systems in zones means that visibility and controllability of the zone is lost: in the event of a fault the control room is unable to perform switching to restore supply. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_02.02.46 | SCADA Schemes - ZN & TS | 1700786129 | REP SCADA SYSTEM ZN00342 PADDINGTON | 1 | 431324.2203 | 431324.2203 | 2025 | PADDINGTON | Ausgrid has numerous unsupported proprietary SCADA systems and components installed in sub-transmission, zone and distribution substations that are now beyond their standard technical life. In all cases the maintenance and support (including replacement parts) has ceased for these legacy systems (those identified for replacement) as the hardware components are no longer available. Ausgrid’s legacy proprietary SCADA equipment also cannot support modern feeder protection relays will not support the enablement of future network capability including the Advanced Distribution Management System (ADMS). Failure of SCADA systems in zones means that visibility and controllability of the zone is lost: in the event of a fault the control room is unable to perform switching to restore supply.
REP_02.02.59 | Neutral Earthing Resistors - ZN & TS | 1700374870 | REP NER R1 TS00402 ERARING | 1 | 457188.4964 | 457188.4964 | 2025 | ERARING | These are approaching end of life and have hidden failure modes. Failure of these assets delays fault clearing and reduces the life of related switchgear. | 2025 | No Change
REP_02.02.59 | Neutral Earthing Resistors - ZN & TS | 1700756324 | REP NER R2 TS00402 ERARING | 1 | 457188.4964 | 457188.4964 | 2025 | ERARING | These are approaching end of life and have hidden failure modes. Failure of these assets delays fault clearing and reduces the life of related switchgear. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700201345 | REP 97m CONSAC S005200_2 ANGEL ST & SLCP | 0.13 | 1765426.1973 | 229505.4056 | 2025 | NEWTOWN | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700201697 | REP 208m CONSAC S006841_1 OBSERVATORY HI | 0.21 | 1765426.1973 | 370739.5014 | 2025 | MILLERS POINT | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700201876 | REP 189m CONSAC S000051_3 HARCOURT PDE & | 0.21 | 1765426.1973 | 370739.5014 | 2025 | ROSEBERY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700201954 | REP 122m CONSAC S001344_1 MIRRABOOKA CRE | 0.19 | 1765426.1973 | 335430.9775 | 2025 | LITTLE BAY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700202033 | REP 218m CONSAC S002899_3 WALKER ST E U | 0.12 | 1765426.1973 | 211851.1437 | 2025 | NORTH SYDNEY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700202286 | REP 102m CONSAC S001040_3 BOORAGUL ST S | 0.22 | 1765426.1973 | 388393.7634 | 2025 | BEVERLY HILLS | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700202771 | REP 109m CONSAC S004567_7 GOSBELL ST | 0.48 | 1765426.1973 | 847404.5747 | 2025 | DARLINGHURST | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700203081 | REP 83m CONSAC S000111_3 JABEZ ST WEST | 0.23 | 1765426.1973 | 406048.0254 | 2025 | MARRICKVILLE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700203248 | REP 164m CONSAC S002600_2 BELCOTE RD | 0.25 | 1765426.1973 | 441356.5493 | 2025 | LONGUEVILLE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700203253 | REP 157m CONSAC S000096_5 KINTORE ST | 0.16 | 1765426.1973 | 282468.1916 | 2025 | DULWICH HILL | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700203397 | REP 71m CONSAC S005800_1 TWEEDMOUTH AVE | 0.16 | 1765426.1973 | 282468.1916 | 2025 | ROSEBERY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700203650 | REP 465m CONSAC S009839_3 NULLABOR PL U | 0.19 | 1765426.1973 | 335430.9775 | 2025 | YARRAWARRAH | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700203663 | REP 160m CONSAC S002139_4 NORTH TERRACE | 0.47 | 1765426.1973 | 829750.3127 | 2025 | BANKSTOWN | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700203847 | REP 78m CONSAC S002352_3 STANLEY ST | 0.16 | 1765426.1973 | 282468.1916 | 2025 | CAMPSIE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700203944 | REP 172m CONSAC S000135_3 WILLIAM NEW | 0.32 | 1765426.1973 | 564936.3831 | 2025 | DOUBLE BAY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700203997 | REP 55m CONSAC S010253_3 MONOMEETH ST N | 0.17 | 1765426.1973 | 300122.4535 | 2025 | BEXLEY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700204122 | REP 31m CONSAC S006045_2 BERYL AV EAST | 0.14 | 1765426.1973 | 247159.6676 | 2025 | MOUNT COLAH | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700204146 | REP 91m CONSAC S000096_3 NEW CANTERBURY | 0.31 | 1765426.1973 | 547282.1211 | 2025 | DULWICH HILL | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700204357 | REP 125m CONSAC S002199_4 WILLIAM ST NW | 0.12 | 1765426.1973 | 211851.1437 | 2025 | WOOLLOOMOOLOO | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700204369 | REP 129m CONSAC S000020_1 MITCHELL RD NT | 0.13 | 1765426.1973 | 229505.4056 | 2025 | ALEXANDRIA | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700204498 | REP 112m CONSAC S000051_2 ROTHSCHILD AV | 0.13 | 1765426.1973 | 229505.4056 | 2025 | ROSEBERY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700204773 | REP 13m CONSAC S000135_1 NEW STH.HEAD R | 0.26 | 1765426.1973 | 459010.8113 | 2025 | DOUBLE BAY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700204893 | REP 120m CONSAC S000241_3 NICHOLSON ST | 0.17 | 1765426.1973 | 300122.4535 | 2025 | BURWOOD | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700204908 | REP 177m CONSAC S002960_1 KIPPAX ST W OH | 0.12 | 1765426.1973 | 211851.1437 | 2025 | SURRY HILLS | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700204922 | REP 138m CONSAC S000135_5 STAFFORD ST UG | 0.18 | 1765426.1973 | 317776.7155 | 2025 | DOUBLE BAY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700204983 | REP 77m CONSAC S000119_3 GLEBE PT RD UG | 0.14 | 1765426.1973 | 247159.6676 | 2025 | GLEBE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700205163 | REP 125m CONSAC S000104_5 NICHOLSON ST N | 0.31 | 1765426.1973 | 547282.1211 | 2025 | WOOLLOOMOOLOO | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700205289 | REP 194m CONSAC S002031_2 CONCORD RD NTH | 0.13 | 1765426.1973 | 229505.4056 | 2025 | RHODES | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700205431 | REP 194m CONSAC PT10895_1 FOREST RD STH | 0.19 | 1765426.1973 | 335430.9775 | 2025 | LUGARNO | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700205490 | REP 45m CONSAC S000172_1 FLETCHER ST & S | 0.19 | 1765426.1973 | 335430.9775 | 2025 | BONDI | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700823573 | REP 10m CONSAC S009777_2 URANA RD W N | 0.17 | 1765426.1973 | 300122.4535 | 2025 | YARRAWARRAH | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700240471 | REP 80m HDPE S000111_2 SHEPHERD ST NORTH | 0.16 | 1765426.1973 | 282468.1916 | 2025 | MARRICKVILLE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700240609 | REP 78m HDPE S001320_3 VORE ST & S.8145 | 0.18 | 1765426.1973 | 317776.7155 | 2025 | SILVERWATER | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700240880 | REP 58m HDPE S002340_1 PUNCHBOWL RD WEST | 0.12 | 1765426.1973 | 211851.1437 | 2025 | LAKEMBA | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700241807 | REP 56m HDPE S001040_1 ALLAMBEE CRES | 0.13 | 1765426.1973 | 229505.4056 | 2025 | BEVERLY HILLS | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354231 | DOC LV RECONFIG SLCP3045 POLE BA00501 | 11.82 | 33237.7097 | 392869.7289 | 2026 | LILLI PILLI | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354248 | 0.300V RECONFIG SLCP354 POLE MO30407 | 8.168 | 33237.7097 | 271485.613 | 2026 | BALGOWLAH | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354264 | DOC LV RECONFIG SLCP921 POLE EP13303 | 8.652 | 33237.7097 | 287572.6645 | 2026 | WESTLEIGH | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354296 | DOC LV RECONFIG SLCP157 POLE GL57886 | 6.449 | 33237.7097 | 214349.99 | 2026 | HUNTERS HILL | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354299 | DOC LV RECONFIG SLCPNR POLE CR06923 | 7.214 | 33237.7097 | 239776.8379 | 2026 | SYLVANIA WATERS | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354319 | DOC LV RECONFIG SLCP19 POLE PY20216 | 7.829 | 33237.7097 | 260218.0294 | 2026 | TURRAMURRA | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354334 | DOC LV RECONFIG SLCP872 POLE PY30646 | 7.777 | 33237.7097 | 258489.6685 | 2026 | MARSFIELD | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354360 | DOC LV RECONFIG SLCP3024 POLE CR08661 | 6.424 | 33237.7097 | 213519.0472 | 2026 | SYLVANIA | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354361 | DOC LV RECONFIG SLCP3012 POLE SU01785 | 8.678 | 33237.7097 | 288436.8449 | 2026 | ENGADINE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354388 | DOC LV RECONFIG SLCP969 POLE RP23679 | 12.38 | 33237.7097 | 411482.8463 | 2026 | BERALA | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354400 | DOC LV RECONFIG SLCP405 POLE EP24347 | 6.459 | 33237.7097 | 214682.3671 | 2026 | EASTWOOD | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354410 | DOC LV RECONFIG SLCP3011 POLE EN00405 | 10.007 | 33237.7097 | 332609.7612 | 2026 | ENGADINE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354425 | DOC LV RECONFIG SLCP536 POLE MO02212 | 7.333 | 33237.7097 | 243732.1254 | 2026 | NORTH WILLOUGHBY | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354441 | DOC LV RECONFIG SLCP3058 POLE KL00203 | 6.12 | 33237.7097 | 203414.7835 | 2026 | KURNELL | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354442 | DOC LV RECONFIG SLCP665 POLE RP05887 | 6.788 | 33237.7097 | 225617.5736 | 2026 | STRATHFIELD | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354466 | DOC LV RECONFIG SLCP3035 POLE SU13079 | 7.541 | 33237.7097 | 250645.569 | 2026 | GYMEA BAY | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354479 | DOC LV RECONFIG SLCP519 POLE GL33045 | 9.859 | 33237.7097 | 327690.5801 | 2027 | NORTH RYDE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354491 | DOC LV RECONFIG SLCP146 POLE PY31755 | 6.939 | 33237.7097 | 230636.4677 | 2027 | EASTWOOD | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354504 | DOC LV RECONFIG SLCP356 POLE GL04369 | 10.549 | 33237.7097 | 350624.5998 | 2027 | CONCORD | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354513 | DOC LV RECONFIG SLCP717 POLE EP76987 | 7.105 | 33237.7097 | 236153.9276 | 2027 | CARLINGFORD | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354545 | DOC LV RECONFIG SLCP3050 POLE CR00564 | 6.074 | 33237.7097 | 201885.8488 | 2027 | CARINGBAH | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354599 | DOC LV RECONFIG SLCP412 POLE EP74023 | 7.53 | 33237.7097 | 250279.9542 | 2027 | NORTH EPPING | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354635 | DOC LV RECONFIG SLCP3576 POLE SU02783 | 6.282 | 33237.7097 | 208799.2925 | 2027 | LOFTUS | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354654 | DOC LV RECONFIG SLCP3025 POLE SU10882 | 7.231 | 33237.7097 | 240341.879 | 2027 | OYSTER BAY | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354686 | DOC LV RECONFIG SLCP523 POLE EP17340 | 6.549 | 33237.7097 | 217673.761 | 2027 | PENNANT HILLS | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354749 | DOC LV RECONFIG SLCP3029 POLE SU00740 | 10.363 | 33237.7097 | 344442.3858 | 2027 | COMO | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354886 | DOC LV RECONFIG SLCP573 POLE MO47770 | 6.847 | 33237.7097 | 227578.5984 | 2028 | NORTHBRIDGE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354950 | DOC LV RECONFIG SLCP3034 POLE SU14116 | 8.246 | 33237.7097 | 274078.1543 | 2028 | MIRANDA | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700354986 | DOC LV RECONFIG SLCP3095 POLE SU02460 | 6.311 | 33237.7097 | 209763.186 | 2028 | ENGADINE | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700355109 | DOC LV RECONFIG SLCP512 POLE LE12758 | 6.581 | 33237.7097 | 218737.3677 | 2028 | BALMAIN | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700355299 | DOC LV RECONFIG SLCP3046 POLE CR07098 | 7.062 | 33237.7097 | 234724.706 | 2028 | CARINGBAH SOUTH | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700355311 | DOC LV RECONFIG SLCP3041 POLE CR01494 | 6.421 | 33237.7097 | 213419.3341 | 2028 | CARINGBAH | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.73 | Dedicated LV Circuit Reconfiguration | 1700732550 | DOC LV RECONFIG SLCPNR POLE BU02612 | 6.43 | 33237.7097 | 213718.4735 | 2029 | HALEKULANI | The need for this LV circuit reconfiguration program is primarily driven by circuit condition and inherent design issues which have resulted in safety risks to the public, customers or workers when the dedicated street lighting circuits fail and remain live in a position where contact can be made with the circuit. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
DOC_11.03.78 | Decommission CBD Vault | 1700735417 | DECOM S000428 Bridge & George | 1 | 731872.6131 | 731872.6131 | 2026 | SYDNEY | Several underground or vault distribution substations located in the Sydney CBD network area are no longer required, with no plans to rebuild a distribution substation on site for the foreseeable future. To prevent these sites from becoming a safety hazard for Ausgrid’s personnel and the public, there is an obligation to disconnect cables, dismantle equipment and remediate the sites. | 2026 | No Change
REP_01.02.61 | Intertripping Schemes - DC | 1700438688 | REP 11KV IT PROT S000123 JOHNSON QUEEN | 1 | 232547.173 | 232547.173 | 2026 | ALEXANDRIA | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.61 | Intertripping Schemes - DC | 1700438696 | REP 11KV IT PROT S002420 BANKSTOWN SQUAR | 1 | 232547.173 | 232547.173 | 2026 | BANKSTOWN | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.61 | Intertripping Schemes - DC | 1700438698 | REP 11KV IT PROT S002533 GOLDMAN LANE | 1 | 232547.173 | 232547.173 | 2026 | DOUBLE BAY | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.61 | Intertripping Schemes - DC | 1700438701 | REP 11KV IT PROT S002582 ANZAC WAL | 1 | 232547.173 | 232547.173 | 2026 | KINGSFORD | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.61 | Intertripping Schemes - DC | 1700438702 | REP 11KV IT PROT S002797 FREDERICK HERBE | 1 | 232547.173 | 232547.173 | 2026 | ARTARMON | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.61 | Intertripping Schemes - DC | 1700438704 | REP 11KV IT PROT S003002 ARTHUR MOUNT NO | 1 | 232547.173 | 232547.173 | 2026 | NORTH SYDNEY | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.61 | Intertripping Schemes - DC | 1700438705 | REP 11KV IT PROT S002975 CLIFF LAVENDER | 1 | 232547.173 | 232547.173 | 2027 | MILSONS POINT | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.61 | Intertripping Schemes - DC | 1700438706 | REP 11KV IT PROT S002959 KIPPAX HOLT NO | 1 | 232547.173 | 232547.173 | 2027 | SURRY HILLS | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.61 | Intertripping Schemes - DC | 1700438707 | REP 11KV IT PROT S003239 MEREWETHER BUIL | 1 | 232547.173 | 232547.173 | 2027 | DARLINGTON | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.61 | Intertripping Schemes - DC | 1700438709 | REP 11KV IT PROT S003167 NEW MCLEAN ST | 1 | 232547.173 | 232547.173 | 2027 | EDGECLIFF | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.61 | Intertripping Schemes - DC | 1700438710 | REP 11KV IT PROT S003542 LOVE NB NO 1 | 1 | 232547.173 | 232547.173 | 2027 | STRATHFIELD SOUTH | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.61 | Intertripping Schemes - DC | 1700438713 | REP 11KV IT PROT S003718 HILL AGL CENTRE | 1 | 232547.173 | 232547.173 | 2027 | NORTH SYDNEY | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2027 | No Change
REP_01.02.61 | Intertripping Schemes - DC | 1700438714 | REP 11KV IT PROT S002960 KIPPAX HOLT NO. | 1 | 232547.173 | 232547.173 | 2028 | SURRY HILLS | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.61 | Intertripping Schemes - DC | 1700438715 | REP 11KV IT PROT S003666 MECH. ENGINEERI | 1 | 232547.173 | 232547.173 | 2028 | DARLINGTON | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.61 | Intertripping Schemes - DC | 1700438718 | REP 11KV IT PROT S003915 MILLER NORTHPOI | 1 | 232547.173 | 232547.173 | 2028 | NORTH SYDNEY | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2028 | No Change
REP_01.02.61 | Intertripping Schemes - DC | 1700438719 | REP 11KV IT PROT S003762 GEORGE PORT | 1 | 232547.173 | 232547.173 | 2028 | WATERLOO | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2028 | No Change
REP_01.02.61 | Intertripping Schemes - DC | 1700438720 | REP 11KV IT PROT S004186 EASTWOOD SHOPPI | 1 | 232547.173 | 232547.173 | 2028 | EASTWOOD | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2028 | No Change
REP_01.02.61 | Intertripping Schemes - DC | 1700438722 | REP 11KV IT PROT S004590 CARROLL LANE | 1 | 232547.173 | 232547.173 | 2028 | BONDI JUNCTION | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2028 | No Change
REP_01.02.61 | Intertripping Schemes - DC | 1700438724 | REP 11KV IT PROT S005325 WATERLOO MACQUA | 1 | 232547.173 | 232547.173 | 2029 | MACQUARIE PARK | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life. | 2028 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.02.61 | Intertripping Schemes - DC | 1700438725 | REP 11KV IT PROT S005326 WATERLOO MACQUA | 1 | 232547.173 | 232547.173 | 2029 | MACQUARIE PARK | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life.
REP_01.02.61 | Intertripping Schemes - DC | 1700438728 | REP 11KV IT PROT S006235 LITTLE WALKER M | 1 | 232547.173 | 232547.173 | 2029 | NORTH SYDNEY | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life.
REP_01.02.61 | Intertripping Schemes - DC | 1700438730 | REP 11KV IT PROT S006388 SPRING WESTFIEL | 1 | 232547.173 | 232547.173 | 2029 | CHATSWOOD | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life.
REP_01.02.61 | Intertripping Schemes - DC | 1700438732 | REP 11KV IT PROT S006445 DARLING HARBOUR | 1 | 232547.173 | 232547.173 | 2029 | SYDNEY | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life.
REP_01.02.61 | Intertripping Schemes - DC | 1700438733 | REP 11KV IT PROT S006494 RICKARD APPIAN | 1 | 232547.173 | 232547.173 | 2029 | BANKSTOWN | A significant portion of Ausgrid's relays utilise electromechanical technology. These fail predominantly in a manner that is not immediately detected (hidden failure modes). The implication of hidden failure modes is that they remain undetected until the asset is required to operate at which time the relay fails to perform its function. Furthermore, many of the older relays are no longer supported by manufacturers and spare parts are not readily available and a reactive replacement would require a technology change which is time consuming to implement. Intertripping schemes are completely dependent upon the degrading pilot wire network. The failure modes of pilot wires are hidden and remain undetected until required to operate. These assets also experience high levels of degraded insulation and mechanical damage. These assets are considered to be at the end of their standard technical life.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700175810 | REP NALDER NP_1 S000843 KENT & KING STS | 1 | 422597.0516 | 422597.0516 | 2026 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700175815 | REP NALDER NP_1 S000414 CLARENCE MARGARE | 1 | 422597.0516 | 422597.0516 | 2026 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700311949 | REP NALDER NP_2 S000414 CLARENCE & MARGA | 1 | 422597.0516 | 422597.0516 | 2026 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700311953 | REP NALDER NP_2 S000843 KENT & KING STS | 1 | 422597.0516 | 422597.0516 | 2026 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700311950 | REP NALDER NP_3 S000414 CLARENCE & MARGA | 1 | 422597.0516 | 422597.0516 | 2026 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700311954 | REP NALDER NP_3 S000843 KENT & KING STS | 1 | 422597.0516 | 422597.0516 | 2026 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700175825 | REP GE OLD NP_1 S000428 BRIDGE & GEORGE | 1 | 422597.0516 | 422597.0516 | 2026 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700311988 | REP WEST CM2 NP_1 S000842 CASTLEREAGH & | 1 | 422597.0516 | 422597.0516 | 2026 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700311989 | REP WEST CM2 NP_2 S000842 CASTLEREAGH & | 1 | 422597.0516 | 422597.0516 | 2026 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700311990 | REP WEST CM2 NP_3 S000842 CASTLEREAGH & | 1 | 422597.0516 | 422597.0516 | 2026 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700311996 | REP WEST CM2 NP_1 S001036 KING ST SYDNEY | 1 | 422597.0516 | 422597.0516 | 2026 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700311997 | REP WEST CM2 NP_2 S001036 KING ST SYDNEY | 1 | 422597.0516 | 422597.0516 | 2026 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700311998 | REP WEST CM2 NP_3 S001036 KING ST SYDNEY | 1 | 422597.0516 | 422597.0516 | 2026 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2026 | No Change
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312002 | REP WEST CM2 NP_1 S001903 JAMES HARDIE A | 1 | 422597.0516 | 422597.0516 | 2026 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2026 | No Change
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312003 | REP WEST CM2 NP_2 S001903 JAMES HARDIE A | 1 | 422597.0516 | 422597.0516 | 2026 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2026 | No Change
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312009 | REP GE OLD NP_2 S000428 BRIDGE & GEORGE | 1 | 422597.0516 | 422597.0516 | 2027 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312010 | REP GE OLD NP_3 S000428 BRIDGE & GEORGE | 1 | 422597.0516 | 422597.0516 | 2027 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312021 | REP GE OLD NP_1 S001019 O'CONNELL ST BRO | 1 | 422597.0516 | 422597.0516 | 2027 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312022 | REP GE OLD NP_2 S001019 O'CONNELL ST BRO | 1 | 422597.0516 | 422597.0516 | 2027 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312023 | REP GE OLD NP_3 S001019 O'CONNELL ST BRO | 1 | 422597.0516 | 422597.0516 | 2027 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312024 | REP GE OLD NP_1 S001020 KENT & MARKET ST | 1 | 422597.0516 | 422597.0516 | 2027 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312025 | REP GE OLD NP_2 S001020 KENT & MARKET ST | 1 | 422597.0516 | 422597.0516 | 2027 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312026 | REP GE OLD NP_3 S001020 KENT & MARKET ST | 1 | 422597.0516 | 422597.0516 | 2027 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312027 | REP GE MG9 NP_1 S001339 PITT ST ADAMS HO | 1 | 422597.0516 | 422597.0516 | 2027 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312028 | REP GE MG9 NP_2 S001339 PITT ST ADAMS HO | 1 | 422597.0516 | 422597.0516 | 2027 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312029 | REP GE MG9 NP_3 S001339 PITT ST ADAMS HO | 1 | 422597.0516 | 422597.0516 | 2027 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312033 | REP GE OLD NP_1 S002028 LA SALLE KING ST | 1 | 422597.0516 | 422597.0516 | 2027 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2027 | No Change
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312034 | REP GE OLD NP_2 S002028 LA SALLE KING ST | 1 | 422597.0516 | 422597.0516 | 2027 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2027 | No Change
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312035 | REP GE OLD NP_3 S002028 LA SALLE KING ST | 1 | 422597.0516 | 422597.0516 | 2027 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2027 | No Change
REP_01.03.06 | Network Protectors (West CM2/22) | 1700288073 | DEC WEST CM2 NP_1 S000430 BATHURST & KE | 1 | 422597.0516 | 422597.0516 | 2027 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2027 | No Change
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312055 | REP NILSEN NP_1 S004016 EXCHGE CTR PITT | 1 | 422597.0516 | 422597.0516 | 2027 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2027 | No Change
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312056 | REP NILSEN NP_2 S004016 EXCHGE CTR PITT | 1 | 422597.0516 | 422597.0516 | 2028 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312057 | REP NILSEN NP_3 S004016 EXCHGE CTR PITT | 1 | 422597.0516 | 422597.0516 | 2028 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312070 | REP WEST CM22 NP_2 S000430 BATHURST & KE | 1 | 422597.0516 | 422597.0516 | 2028 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312071 | REP WEST CM22 NP_3 S000430 BATHURST & KE | 1 | 422597.0516 | 422597.0516 | 2028 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312072 | REP WEST CM22 NP_1 S000431 ELIZ ST ST JA | 1 | 422597.0516 | 422597.0516 | 2028 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312073 | REP WEST CM22 NP_2 S000431 ELIZ ST ST JA | 1 | 422597.0516 | 422597.0516 | 2028 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2028 | No Change
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312074 | REP WEST CM22 NP_3 S000431 ELIZ ST ST JA | 1 | 422597.0516 | 422597.0516 | 2028 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2028 | No Change
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312075 | REP WEST CM22 NP_1 S000541 DRUITT & CLAR | 1 | 422597.0516 | 422597.0516 | 2028 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2028 | No Change
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312076 | REP WEST CM22 NP_2 S000541 DRUITT & CLAR | 1 | 422597.0516 | 422597.0516 | 2028 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2028 | No Change
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312077 | REP WEST CM22 NP_3 S000541 DRUITT & CLAR | 1 | 422597.0516 | 422597.0516 | 2028 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2028 | No Change
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312096 | REP WEST CM22 NP_1 S000908 CASTLERGH & H | 1 | 422597.0516 | 422597.0516 | 2028 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2028 | No Change
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312097 | REP WEST CM22 NP_2 S000908 CASTLERGH & H | 1 | 422597.0516 | 422597.0516 | 2028 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2028 | No Change
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312098 | REP WEST CM22 NP_3 S000908 CASTLERGH & H | 1 | 422597.0516 | 422597.0516 | 2028 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2028 | No Change
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312113 | REP WEST CM22 NP_1 S001041 JAMISON & CLA | 1 | 422597.0516 | 422597.0516 | 2028 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2028 | No Change
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312114 | REP WEST CM22 NP_2 S001041 JAMISON & CLA | 1 | 422597.0516 | 422597.0516 | 2028 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2028 | No Change
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312115 | REP WEST CM22 NP_3 S001041 JAMISON & CLA | 1 | 422597.0516 | 422597.0516 | 2028 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2028 | No Change
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312119 | REP WEST CM22 NP_1 S001008 YORK & KING S | 1 | 422597.0516 | 422597.0516 | 2029 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2028 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312120 | REP WEST CM22 NP_2 S001008 YORK & KING S | 1 | 422597.0516 | 422597.0516 | 2029 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers. | 2028 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312121 | REP WEST CM22 NP_3 S001008 YORK & KING S | 1 | 422597.0516 | 422597.0516 | 2029 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312124 | REP WEST CM22 NP_1 S001018 ERSKINE & CLA | 1 | 422597.0516 | 422597.0516 | 2029 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312125 | REP WEST CM22 NP_2 S001018 ERSKINE & CLA | 1 | 422597.0516 | 422597.0516 | 2029 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312126 | REP WEST CM22 NP_3 S001018 ERSKINE & CLA | 1 | 422597.0516 | 422597.0516 | 2029 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312133 | REP WEST CM22 NP_1 S000863 MACQUARIE ST | 1 | 422597.0516 | 422597.0516 | 2029 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312134 | REP WEST CM22 NP_2 S000863 MACQUARIE ST | 1 | 422597.0516 | 422597.0516 | 2029 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312135 | REP WEST CM22 NP_3 S000863 MACQUARIE ST | 1 | 422597.0516 | 422597.0516 | 2029 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312142 | REP WEST CM2 NP_1 S000836 SONY HOUSE DRU | 1 | 422597.0516 | 422597.0516 | 2029 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312143 | REP WEST CM2 NP_2 S000836 SONY HOUSE DRU | 1 | 422597.0516 | 422597.0516 | 2029 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312144 | REP WEST CM22 NP_3 S000836 SONY HOUSE DR | 1 | 422597.0516 | 422597.0516 | 2029 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312168 | REP WEST CM22 NP_1 S001784 RESERVE BK 1 | 1 | 422597.0516 | 422597.0516 | 2029 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312169 | REP WEST CM22 NP_2 S001784 RESERVE BK 1 | 1 | 422597.0516 | 422597.0516 | 2029 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312170 | REP WEST CM22 NP_3 S001784 RESERVE BK 1 | 1 | 422597.0516 | 422597.0516 | 2029 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers.
REP_01.03.06 | Network Protectors (West CM2/22) | 1700312171 | REP WEST CM22 NP_1 S002041 BLIGH HOUSE B | 1 | 422597.0516 | 422597.0516 | 2029 | SYDNEY | Network protectors are a type of Circuit Breaker which is unique to Ausgrid CBD Triplex distribution network. Most of these assets are over 50 years old, include some which are over 70 years old. Failures of these assets are mainly due to supply trip mechanism. The failure of this equipment can cause loss of supply to customers. Compromised protection also increases risks associated with damage to primary transformers.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261417 | REP CBDTX_T3 S000836 Sony House Druitt | 1 | 393740.0984 | 393740.0984 | 2026 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261419 | REP CBDTX_T2 S000979 Elizabeth & King St | 1 | 393740.0984 | 393740.0984 | 2026 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261422 | REP CBDTX_T1 S000979 Elizabeth & King St | 1 | 393740.0984 | 393740.0984 | 2026 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261425 | REP CBDTX_T3 S000979 Elizabeth & King St | 1 | 393740.0984 | 393740.0984 | 2026 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261431 | REP CBDTX_T1 S001903 James Hardie Albert | 1 | 393740.0984 | 393740.0984 | 2026 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2026 | No Change
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261434 | REP CBDTX_T2 S001036 King St Sydney Arca | 1 | 393740.0984 | 393740.0984 | 2027 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261435 | REP CBDTX_T2 S001020 Kent & Market Sts | 1 | 393740.0984 | 393740.0984 | 2027 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261436 | REP CBDTX_T3 S001020 Kent & Market Sts | 1 | 393740.0984 | 393740.0984 | 2027 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261437 | REP CBDTX_T2 S001903 James Hardie Albert | 1 | 393740.0984 | 393740.0984 | 2027 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2027 | No Change
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261438 | REP CBDTX_T3 S001036 King St Sydney Arca | 1 | 393740.0984 | 393740.0984 | 2027 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2027 | No Change
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261439 | REP CBDTX_T2 S001019 O'connell St Brook | 1 | 393740.0984 | 393740.0984 | 2027 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2027 | No Change
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261440 | REP CBDTX_T3 S001019 O'connell St Brook | 1 | 393740.0984 | 393740.0984 | 2028 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261441 | REP CBDTX_T1 S001036 King St Sydney Arca | 1 | 393740.0984 | 393740.0984 | 2028 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261452 | REP CBDTX_T1 S000842 Castlereagh & Park | 1 | 393740.0984 | 393740.0984 | 2028 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2028 | No Change
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261453 | REP CBDTX_T2 S000842 Castlereagh & Park | 1 | 393740.0984 | 393740.0984 | 2028 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2028 | No Change
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261454 | REP CBDTX_T1 S000836 Sony House Druitt | 1 | 393740.0984 | 393740.0984 | 2028 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2028 | No Change
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261456 | REP CBDTX_T2 S000836 Sony House Druitt | 1 | 393740.0984 | 393740.0984 | 2028 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures. | 2028 | No Change
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261458 | REP CBDTX_T2 S000863 Macquarie St Martin | 1 | 393740.0984 | 393740.0984 | 2029 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261464 | REP CBDTX_T3 S000842 Castlereagh & Park | 1 | 393740.0984 | 393740.0984 | 2029 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261465 | REP CBDTX_T1 S000863 Macquarie St Martin | 1 | 393740.0984 | 393740.0984 | 2029 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261466 | REP CBDTX_T3 S000863 Macquarie St Martin | 1 | 393740.0984 | 393740.0984 | 2029 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700261468 | REP CBDTX_T1 S001019 O'connell St Brook | 1 | 393740.0984 | 393740.0984 | 2029 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures.
REP_01.03.07 | 400kVA Sydney CBD Conservator Type Tx | 1700263964 | REP CBDTX_T2 S000428 Bridge & George Sts | 1 | 393740.0984 | 393740.0984 | 2029 | SYDNEY | The majority of Ausgrid's distribution transformers are filled with oil for cooling and insulation purposes. The need for replacement is driven by the risks associated with a functional failure of Sydney CBD distribution transformers. Deterioration of these assets over time has led to a number of functional failures.
REP_01.03.13 | Bass & Saunders Isolation & Earthing Swit | 1700208977 | REP HV B&S I&E - S000428 BRIDGE & GEORGE | 3 | 266808.3928 | 266808.3928 | 2026 | SYDNEY | The major issue with these assets relates to operating restrictions associated with the condition of the asset. The switch is not spring assisted and results in WH&S issues for network operators. Moreover, since their switching capacity cannot be determined, incoming feeders must be de-energised to operate the switch, which increases the time and cost of network switching. Projects have been identified based on a condition assessment. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.13 | Bass & Saunders Isolation & Earthing Swit | 1700208978 | REP HV B&S I&E - S000430 BATHURST & KENT | 3 | 266808.3928 | 266808.3928 | 2026 | SYDNEY | The major issue with these assets relates to operating restrictions associated with the condition of the asset. The switch is not spring assisted and results in WH&S issues for network operators. Moreover, since their switching capacity cannot be determined, incoming feeders must be de-energised to operate the switch, which increases the time and cost of network switching. Projects have been identified based on a condition assessment. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.13 | Bass & Saunders Isolation & Earthing Swit | 1700208991 | REP HV B&S I&E - S000836 SONY HOUSE DRUI | 3 | 266808.3928 | 266808.3928 | 2027 | SYDNEY | The major issue with these assets relates to operating restrictions associated with the condition of the asset. The switch is not spring assisted and results in WH&S issues for network operators. Moreover, since their switching capacity cannot be determined, incoming feeders must be de-energised to operate the switch, which increases the time and cost of network switching. Projects have been identified based on a condition assessment. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.13 | Bass & Saunders Isolation & Earthing Swit | 1700208993 | REP HV B&S I&E - S000841 SUSSEX & GOULBU | 3 | 266808.3928 | 266808.3928 | 2027 | SYDNEY | The major issue with these assets relates to operating restrictions associated with the condition of the asset. The switch is not spring assisted and results in WH&S issues for network operators. Moreover, since their switching capacity cannot be determined, incoming feeders must be de-energised to operate the switch, which increases the time and cost of network switching. Projects have been identified based on a condition assessment. | 2027 | No Change
REP_01.03.13 | Bass & Saunders Isolation & Earthing Swit | 1700208994 | REP HV B&S I&E - S000842 CASTLEREAGH & P | 3 | 266808.3928 | 266808.3928 | 2028 | SYDNEY | The major issue with these assets relates to operating restrictions associated with the condition of the asset. The switch is not spring assisted and results in WH&S issues for network operators. Moreover, since their switching capacity cannot be determined, incoming feeders must be de-energised to operate the switch, which increases the time and cost of network switching. Projects have been identified based on a condition assessment. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.13 | Bass & Saunders Isolation & Earthing Swit | 1700208995 | REP HV B&S I&E - S000843 KENT & KING STS | 3 | 266808.3928 | 266808.3928 | 2028 | SYDNEY | The major issue with these assets relates to operating restrictions associated with the condition of the asset. The switch is not spring assisted and results in WH&S issues for network operators. Moreover, since their switching capacity cannot be determined, incoming feeders must be de-energised to operate the switch, which increases the time and cost of network switching. Projects have been identified based on a condition assessment. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.13 | Bass & Saunders Isolation & Earthing Swit | 1700209000 | REP HV B&S I&E - S000856 PITT & HUNTER S | 3 | 266808.3928 | 266808.3928 | 2029 | SYDNEY | The major issue with these assets relates to operating restrictions associated with the condition of the asset. The switch is not spring assisted and results in WH&S issues for network operators. Moreover, since their switching capacity cannot be determined, incoming feeders must be de-energised to operate the switch, which increases the time and cost of network switching. Projects have been identified based on a condition assessment. | 2028 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_01.03.13 | Bass & Saunders Isolation & Earthing Swit | 1700209001 | REP HV B&S I&E - S000863 MACQUARIE ST MA | 3 | 266808.3928 | 266808.3928 | 2029 | SYDNEY | The major issue with these assets relates to operating restrictions associated with the condition of the asset. The switch is not spring assisted and results in WH&S issues for network operators. Moreover, since their switching capacity cannot be determined, incoming feeders must be de-energised to operate the switch, which increases the time and cost of network switching. Projects have been identified based on a condition assessment. | 2028 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_02.02.46 | SCADA Schemes - ZN & TS | 1700438527 | REP SCADA SYSTEM TS07150 PYRMONT STS | 1 | 431324.2203 | 431324.2203 | 2026 | PYRMONT | Ausgrid has numerous unsupported proprietary SCADA systems and components installed in sub-transmission, zone and distribution substations that are now beyond their standard technical life. In all cases the maintenance and support (including replacement parts) has ceased for these legacy systems (those identified for replacement) as the hardware components are no longer available. Ausgrid’s legacy proprietary SCADA equipment also cannot support modern feeder protection relays will not support the enablement of future network capability including the Advanced Distribution Management System (ADMS). Failure of SCADA systems in zones means that visibility and controllability of the zone is lost: in the event of a fault the control room is unable to perform switching to restore supply. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_02.02.46 | SCADA Schemes - ZN & TS | 1700438534 | REP SCADA SYSTEM ZN04990 CITY CENTRAL | 1 | 431324.2203 | 431324.2203 | 2027 | SYDNEY | Ausgrid has numerous unsupported proprietary SCADA systems and components installed in sub-transmission, zone and distribution substations that are now beyond their standard technical life. In all cases the maintenance and support (including replacement parts) has ceased for these legacy systems (those identified for replacement) as the hardware components are no longer available. Ausgrid’s legacy proprietary SCADA equipment also cannot support modern feeder protection relays will not support the enablement of future network capability including the Advanced Distribution Management System (ADMS). Failure of SCADA systems in zones means that visibility and controllability of the zone is lost: in the event of a fault the control room is unable to perform switching to restore supply. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_02.02.46 | SCADA Schemes - ZN & TS | 1700501072 | REP SCADA SYSTEM TS07140 BUNNERONG NORTH | 1 | 431324.2203 | 431324.2203 | 2028 | MATRAVILLE | Ausgrid has numerous unsupported proprietary SCADA systems and components installed in sub-transmission, zone and distribution substations that are now beyond their standard technical life. In all cases the maintenance and support (including replacement parts) has ceased for these legacy systems (those identified for replacement) as the hardware components are no longer available. Ausgrid’s legacy proprietary SCADA equipment also cannot support modern feeder protection relays will not support the enablement of future network capability including the Advanced Distribution Management System (ADMS). Failure of SCADA systems in zones means that visibility and controllability of the zone is lost: in the event of a fault the control room is unable to perform switching to restore supply. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_02.02.46 | SCADA Schemes - ZN & TS | 1700660569 | REP SCADA SYSTEM ZN09550 GWAWLEY BAY | 1 | 431324.2203 | 431324.2203 | 2029 | MIRANDA | Ausgrid has numerous unsupported proprietary SCADA systems and components installed in sub-transmission, zone and distribution substations that are now beyond their standard technical life. In all cases the maintenance and support (including replacement parts) has ceased for these legacy systems (those identified for replacement) as the hardware components are no longer available. Ausgrid’s legacy proprietary SCADA equipment also cannot support modern feeder protection relays will not support the enablement of future network capability including the Advanced Distribution Management System (ADMS). Failure of SCADA systems in zones means that visibility and controllability of the zone is lost: in the event of a fault the control room is unable to perform switching to restore supply. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_02.02.59 | Neutral Earthing Resistors - ZN & TS | 1700374868 | REP NER X3 TS07220 WILLOUGHBY | 1 | 457188.4964 | 457188.4964 | 2026 | ARTARMON | These are approaching end of life and have hidden failure modes. Failure of these assets delays fault clearing and reduces the life of related switchgear. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.01 | Steel Mains (km) | 1201633370 | Rusty Steel mains Sev.2 | 130 | 59150.3006 | 7689539.0764 | 2029 | SANDY HOLLOW | Protective galvanised coating of the steel mains and conductor ties degrades with age and can pose environmental risks, such as fires, public safety and failure of supply. Replacement of the steel mains are identified using an condition assessment process that used inspection, spatial risk factors and failure data.
REP_04.02.05 | LV Consac Cables (km); | 1700214277 | REP 491m CONSAC HS52120_1 FERN PLACE | 0.491 | 1765426.1973 | 866824.2629 | 2026 | EAST MAITLAND | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700214278 | REP 478m CONSAC HS52120_2 FERN PLACE | 0.478 | 1765426.1973 | 843873.7223 | 2026 | EAST MAITLAND | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700214276 | REP 226m CONSAC HS24852 SOUTH SEAS DRIVE | 0.226 | 1765426.1973 | 398986.3206 | 2026 | ASHTONFIELD | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700214317 | REP 393m CONSAC HS54095_24922 GREENHILLS | 0.393 | 1765426.1973 | 693812.4955 | 2026 | EAST MAITLAND | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700214251 | REP 170m CONSAC HP46037_46037 ABERGLASSL | 0.17 | 1765426.1973 | 300122.4535 | 2026 | RUTHERFORD | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700214255 | REP 369m CONSAC HP52319_52319 OMARU | 0.369 | 1765426.1973 | 651442.2668 | 2026 | CESSNOCK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700214279 | REP 217m CONSAC HS52120_3 FERN PLACE | 0.217 | 1765426.1973 | 383097.4848 | 2026 | EAST MAITLAND | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700214250 | REP 184m CONSAC HP01685_1685 MAITLAND RD | 0.184 | 1765426.1973 | 324838.4203 | 2026 | BOLWARRA | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700214280 | REP 134m CONSAC HS52120_4 FERN PLACE | 0.134 | 1765426.1973 | 236567.1104 | 2026 | EAST MAITLAND | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2024 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200463 | REP 201m CONSAC S002808_2 SURREY ST S W | 0.201 | 1765426.1973 | 354850.6656 | 2026 | EPPING | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200681 | REP 640m CONSAC S035893_2 CRANBROOK ROAD | 0.64 | 1765426.1973 | 1129872.7662 | 2026 | ROSE BAY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200697 | REP 614m CONSAC S006125_1 SHEPHERDS DR & | 0.614 | 1765426.1973 | 1083971.6851 | 2026 | CHERRYBROOK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200702 | REP 626m CONSAC S005447_2 PARKHILL CRES | 0.626 | 1765426.1973 | 1105156.7995 | 2026 | CHERRYBROOK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700501188 | REP 413m CONSAC S006013_3 KHARTOUM RD E | 0.413 | 1765426.1973 | 729121.0195 | 2026 | MACQUARIE PARK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200705 | REP 581m CONSAC S004020_2 ALVONA AVE E | 0.581 | 1765426.1973 | 1025712.6206 | 2026 | ST IVES | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200710 | REP 205m CONSAC S004944_2 CRAIGLANDS AV | 0.205 | 1765426.1973 | 361912.3704 | 2026 | GORDON | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200716 | REP 399m CONSAC S001796_2 HERRING RD WS | 0.399 | 1765426.1973 | 704405.0527 | 2026 | MARSFIELD | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200722 | REP 442m CONSAC S005345_1 FRANCIS GREEN | 0.442 | 1765426.1973 | 780318.3792 | 2026 | CHERRYBROOK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200723 | REP 526m CONSAC S005570_1 FRANCIS GREEN | 0.526 | 1765426.1973 | 928614.1798 | 2026 | CHERRYBROOK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700488351 | REP 172m CONSAC S005768_2 SHEPHERDS DR | 0.172 | 1765426.1973 | 303653.3059 | 2026 | CHERRYBROOK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200743 | REP 186m CONSAC S002690_3 BOTANY RD EAST | 0.186 | 1765426.1973 | 328369.2727 | 2026 | BANKSMEADOW | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200744 | REP 189m CONSAC S036083_3 WALLEROY RD NT | 0.189 | 1765426.1973 | 333665.5513 | 2026 | WOOLLAHRA | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200754 | REP 566m CONSAC S009675_3 JAMES COOK IS | 0.566 | 1765426.1973 | 999231.2276 | 2026 | SYLVANIA WATERS | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200756 | REP 431m CONSAC S005189_2 SHIPWAY ST E | 0.431 | 1765426.1973 | 760898.691 | 2026 | MARSFIELD | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200758 | REP 130m CONSAC S005036_1 HINEMOA ST & 1 | 0.13 | 1765426.1973 | 229505.4056 | 2026 | PANANIA | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200765 | REP 137m CONSAC S009872_2 TURRIELL PT R | 0.137 | 1765426.1973 | 241863.389 | 2026 | PORT HACKING | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200769 | REP 498m CONSAC S000027_1 S8164,S4104&LY | 0.498 | 1765426.1973 | 879182.2462 | 2027 | MACQUARIE PARK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200771 | REP 210m CONSAC S003799_3 OXFORD ST E N | 0.21 | 1765426.1973 | 370739.5014 | 2027 | EPPING | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200772 | REP 353m CONSAC S001719_2 RAMSGATE AVE U | 0.353 | 1765426.1973 | 623195.4476 | 2027 | NORTH BONDI | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200775 | REP 179m CONSAC S002664_3 CUMBERLAND RD | 0.179 | 1765426.1973 | 316011.2893 | 2027 | AUBURN | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200778 | REP 290m CONSAC S003800_1 CAMBRIDGE ST | 0.29 | 1765426.1973 | 511973.5972 | 2027 | EPPING | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200781 | REP 171m CONSAC S003167_4 CAMERON ST OH | 0.171 | 1765426.1973 | 301887.8797 | 2027 | EDGECLIFF | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200788 | REP 222m CONSAC S005905_3 MARRICKVILLE R | 0.222 | 1765426.1973 | 391924.6158 | 2027 | MARRICKVILLE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200789 | REP 261m CONSAC S001871_1 BALFOUR RD E/N | 0.261 | 1765426.1973 | 460776.2375 | 2027 | BELLEVUE HILL | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200790 | REP 175m CONSAC S001553_3 VICTORIA ST U | 0.175 | 1765426.1973 | 308949.5845 | 2027 | ASHFIELD | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200792 | REP 123m CONSAC S003439_2 BELMORE RD SO | 0.123 | 1765426.1973 | 217147.4223 | 2027 | RANDWICK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700200797 | REP 210m CONSAC S004543_2 CHISWICK RD U | 0.21 | 1765426.1973 | 370739.5014 | 2027 | GREENACRE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200799 | REP 208m CONSAC S004241_2 HEYDON ST _ PA | 0.208 | 1765426.1973 | 367208.649 | 2027 | WARRAWEE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200800 | REP 180m CONSAC S004134_3 MILPERRA RD WE | 0.18 | 1765426.1973 | 317776.7155 | 2027 | REVESBY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200801 | REP 271m CONSAC S002347_3 COORABAN RD | 0.271 | 1765426.1973 | 478430.4995 | 2027 | MILPERRA | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200802 | REP 212m CONSAC S001234_4 HOWARD RD | 0.212 | 1765426.1973 | 374270.3538 | 2027 | PADSTOW | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200803 | REP 211m CONSAC S009780_2 OMARU AVE | 0.211 | 1765426.1973 | 372504.9276 | 2027 | GYMEA | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200804 | REP 279m CONSAC S005046_1 VIRGINIUS ST | 0.279 | 1765426.1973 | 492553.909 | 2027 | PADSTOW | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200805 | REP 223m CONSAC S002347_2 WOORANG ST & | 0.223 | 1765426.1973 | 393690.042 | 2027 | MILPERRA | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200806 | REP 340m CONSAC S002324_6 MOONBIE ST | 0.34 | 1765426.1973 | 600244.9071 | 2027 | SUMMER HILL | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200807 | REP 283m CONSAC S000354_1 BLAIR ST UG & | 0.283 | 1765426.1973 | 499615.6138 | 2027 | BONDI BEACH | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200808 | REP 138m CONSAC S002595_3 WISBEACH ST E | 0.138 | 1765426.1973 | 243628.8152 | 2027 | ROZELLE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200810 | REP 145m CONSAC S001563_3 MOODIE ST | 0.145 | 1765426.1973 | 255986.7986 | 2027 | ROZELLE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200813 | REP 191m CONSAC S009770_2 BURKE RD N W & | 0.191 | 1765426.1973 | 337196.4037 | 2027 | CRONULLA | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200816 | REP 598m CONSAC S004279_3 WAIROA AVE UG | 0.598 | 1765426.1973 | 1055724.866 | 2027 | BONDI | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200819 | REP 948m CONSAC S003954_2 MARCEAU DR SO | 0.948 | 1765426.1973 | 1673624.035 | 2027 | CONCORD | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200820 | REP 309m CONSAC S004903_1 GANMAIN RD UG | 0.309 | 1765426.1973 | 545516.695 | 2027 | PYMBLE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200821 | REP 285m CONSAC S005065_2 WILGA PLACE O | 0.285 | 1765426.1973 | 503146.4662 | 2027 | MARSFIELD | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200822 | REP 274m CONSAC S005582_2 CEDARWOOD DRI | 0.274 | 1765426.1973 | 483726.778 | 2027 | CHERRYBROOK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200824 | REP 116m CONSAC S005156_3 BARKER ST | 0.116 | 1765426.1973 | 204789.4389 | 2027 | LEWISHAM | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700200826 | REP 136m CONSAC S005257_2 MODERN AV | 0.136 | 1765426.1973 | 240097.9628 | 2027 | CANTERBURY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200827 | REP 137m CONSAC S005565_1 MONTAGUE ST | 0.137 | 1765426.1973 | 241863.389 | 2027 | BALMAIN | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200829 | REP 138m CONSAC S000169_8 CHARLECOT ST | 0.138 | 1765426.1973 | 243628.8152 | 2027 | MARRICKVILLE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200836 | REP 185m CONSAC S001880_1 SHARPE ST & S | 0.185 | 1765426.1973 | 326603.8465 | 2027 | BELMORE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700495802 | REP 350m CONSAC S006012_4 MILITARY RD | 0.35 | 1765426.1973 | 617899.169 | 2027 | MOSMAN | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200840 | REP 611m CONSAC S005769_1 WISTERIA CR S | 0.611 | 1765426.1973 | 1078675.4065 | 2028 | CHERRYBROOK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200847 | REP 235m CONSAC S003149_2 THE BOULEVARD | 0.235 | 1765426.1973 | 414875.1564 | 2028 | DULWICH HILL | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200848 | REP 236m CONSAC S002324_2 LUSTRE DRY CL | 0.236 | 1765426.1973 | 416640.5826 | 2028 | SUMMER HILL | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200849 | REP 337m CONSAC S009675_2 JAMES COOK IS | 0.337 | 1765426.1973 | 594948.6285 | 2028 | SYLVANIA WATERS | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200850 | REP 211m CONSAC S077772_3 ADA AVE | 0.211 | 1765426.1973 | 372504.9276 | 2028 | WAHROONGA | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200851 | REP 287m CONSAC S001853_2 HERRING RD UG | 0.287 | 1765426.1973 | 506677.3186 | 2028 | MACQUARIE PARK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200852 | REP 218m CONSAC S003685_4 RAWSON ST EAS | 0.218 | 1765426.1973 | 384862.911 | 2028 | AUBURN | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200853 | REP 133m CONSAC S001753_4 O'CONNELL ST N | 0.133 | 1765426.1973 | 234801.6842 | 2028 | NEWTOWN | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200857 | REP 126m CONSAC S003361_3 CHALEYER ST W | 0.126 | 1765426.1973 | 222443.7009 | 2028 | ROSE BAY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200863 | REP 292m CONSAC S001681_3 WARATAH STREET | 0.292 | 1765426.1973 | 515504.4496 | 2028 | RUSHCUTTERS BAY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200865 | REP 443m CONSAC S007971_2 WELLINGTON ST | 0.443 | 1765426.1973 | 782083.8054 | 2028 | BONDI BEACH | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200866 | REP 544m CONSAC S000354_5 MITCHELL ST W | 0.544 | 1765426.1973 | 960391.8513 | 2028 | BONDI BEACH | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200870 | REP 316m CONSAC S032599_1 MACQUARIE DR | 0.316 | 1765426.1973 | 557874.6783 | 2028 | CHERRYBROOK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200871 | REP 349m CONSAC S005553_1 EDWARD BENNETT | 0.349 | 1765426.1973 | 616133.7428 | 2028 | CHERRYBROOK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200873 | REP 134m CONSAC S009509_3 ANZAC AVE EAS | 0.134 | 1765426.1973 | 236567.1104 | 2028 | ENGADINE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200876 | REP 160m CONSAC S005256_3 ROGAL PL W N | 0.16 | 1765426.1973 | 282468.1916 | 2028 | MACQUARIE PARK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200879 | REP 128m CONSAC S005162_2 MYRA ST | 0.128 | 1765426.1973 | 225974.5532 | 2028 | WAHROONGA | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200881 | REP 121m CONSAC S036227_1 GURNEY RD WES | 0.121 | 1765426.1973 | 213616.5699 | 2028 | CHESTER HILL | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700200891 | REP 187m CONSAC S004530_1 BOTANY RD UG | 0.187 | 1765426.1973 | 330134.6989 | 2028 | BOTANY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200892 | REP 172m CONSAC S001222_1 HUME HWY WEST | 0.172 | 1765426.1973 | 303653.3059 | 2028 | YAGOONA | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200895 | REP 197m CONSAC S000353_6 COUNCIL ST DA | 0.197 | 1765426.1973 | 347788.9609 | 2028 | BONDI JUNCTION | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200897 | REP 422m CONSAC S005928_1 COLLEEN CRES | 0.422 | 1765426.1973 | 745009.8552 | 2028 | CHERRYBROOK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200898 | REP 425m CONSAC S005469_2 CEDARWOOD DR U | 0.425 | 1765426.1973 | 750306.1338 | 2028 | CHERRYBROOK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200900 | REP 240m CONSAC S002648_3 SEBASTAPOL ST | 0.24 | 1765426.1973 | 423702.2873 | 2028 | MARRICKVILLE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200901 | REP 292m CONSAC S000382_2 ADDERLEY ST W | 0.292 | 1765426.1973 | 515504.4496 | 2028 | AUBURN | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200902 | REP 164m CONSAC S003954_3 MARCEAU DR WE | 0.164 | 1765426.1973 | 289529.8963 | 2028 | CONCORD | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200904 | REP 200m CONSAC S007562_2 Ridge St South | 0.2 | 1765426.1973 | 353085.2395 | 2028 | GORDON | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200905 | REP 208m CONSAC S004910_2 CARBEEN AVE | 0.208 | 1765426.1973 | 367208.649 | 2028 | ST IVES | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2028 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200906 | REP 240m CONSAC S005064_2 CLOVELLY RD S | 0.24 | 1765426.1973 | 423702.2873 | 2028 | HORNSBY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2028 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200907 | REP 119m CONSAC S001556_3 LOUDON AV | 0.119 | 1765426.1973 | 210085.7175 | 2028 | HABERFIELD | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700200911 | REP 168m CONSAC S003671_1 COLLEGE ST | 0.168 | 1765426.1973 | 296591.6011 | 2028 | CROYDON | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2028 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200912 | REP 172m CONSAC S003001_2 CHESTER HILL R | 0.172 | 1765426.1973 | 303653.3059 | 2028 | CHESTER HILL | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2028 | No Change
REP_04.02.05 | LV Consac Cables (km); | 1700200917 | REP 118m CONSAC S009866_3 PALM ST | 0.118 | 1765426.1973 | 208320.2913 | 2028 | CARINGBAH SOUTH | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700200919 | REP 125m CONSAC S004248_3 LIVERPOOL ST E | 0.125 | 1765426.1973 | 220678.2747 | 2029 | DARLINGHURST | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700200920 | REP 117m CONSAC S009113_3 GRENVILLE AVE | 0.117 | 1765426.1973 | 206554.8651 | 2029 | CARINGBAH | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700200928 | REP 139m CONSAC S009874_3 CRESCENT RD EA | 0.139 | 1765426.1973 | 245394.2414 | 2029 | CARINGBAH | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2028 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200929 | REP 115m CONSAC S005133_2 EDENSOR ST NO | 0.115 | 1765426.1973 | 203024.0127 | 2029 | EPPING | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700200934 | REP 117m CONSAC S009119_4 GUNNAMATTA RD | 0.117 | 1765426.1973 | 206554.8651 | 2029 | BURRANEER | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700200935 | REP 151m CONSAC S002550_3 WATSON ST NORT | 0.151 | 1765426.1973 | 266579.3558 | 2029 | BONDI | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2028 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200936 | REP 148m CONSAC S005472_2 MALABAR RD NOR | 0.148 | 1765426.1973 | 261283.0772 | 2029 | SOUTH COOGEE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2028 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200939 | REP 154m CONSAC S001709_1 767_771 PACIFI | 0.154 | 1765426.1973 | 271875.6344 | 2029 | GORDON | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2028 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200940 | REP 137m CONSAC S001922_2 RAWSON ST | 0.137 | 1765426.1973 | 241863.389 | 2029 | LIDCOMBE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2028 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200942 | REP 419m CONSAC S002765_3 MILITARY RD UG | 0.419 | 1765426.1973 | 739713.5766 | 2029 | MOSMAN | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2028 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200943 | REP 849m CONSAC S003459_2 CHILDS ST U G | 0.849 | 1765426.1973 | 1498846.8415 | 2029 | LIDCOMBE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2028 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200944 | REP 621m CONSAC S004020_1 ALVONA AVE W | 0.621 | 1765426.1973 | 1096329.6685 | 2029 | ST IVES | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2028 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200945 | REP 635m CONSAC S002381_3 GLEN AYR AVE | 0.635 | 1765426.1973 | 1121045.6353 | 2029 | BONDI BEACH | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2028 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200947 | REP 115m CONSAC S000169_3 WARDELL FAR NO | 0.115 | 1765426.1973 | 203024.0127 | 2029 | MARRICKVILLE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.05 | LV Consac Cables (km); | 1700200954 | REP 192m CONSAC S001716_3 OLD SOUTH HEAD | 0.192 | 1765426.1973 | 338961.8299 | 2029 | BELLEVUE HILL | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2028 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200955 | REP 460m CONSAC S005321_1 MORRIS AVE UG | 0.46 | 1765426.1973 | 812096.0507 | 2029 | THORNLEIGH | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2028 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200956 | REP 519m CONSAC S009811_2 TEA TREE PL N | 0.519 | 1765426.1973 | 916256.1964 | 2029 | KIRRAWEE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2028 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200957 | REP 474m CONSAC S003701_4 EPPING RD UG | 0.474 | 1765426.1973 | 836812.0175 | 2029 | DOUBLE BAY | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2028 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200958 | REP 436m CONSAC S005447_1 PARKHILL CRES | 0.436 | 1765426.1973 | 769725.822 | 2029 | CHERRYBROOK | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2028 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200960 | REP 267m CONSAC S004893_2 ROBINSON ST W | 0.267 | 1765426.1973 | 471368.7947 | 2029 | EAST LINDFIELD | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2028 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200961 | REP 272m CONSAC S000549_1 NO71 PRINCES H | 0.272 | 1765426.1973 | 480195.9257 | 2029 | ST PETERS | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2028 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200962 | REP 204m CONSAC S004433_2 BAY ROAD | 0.204 | 1765426.1973 | 360146.9442 | 2029 | WAVERTON | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2028 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200963 | REP 245m CONSAC S004719_1 BERILDA AVE | 0.245 | 1765426.1973 | 432529.4183 | 2029 | WARRAWEE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2028 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200965 | REP 251m CONSAC S004954_2 DAVIES RD | 0.251 | 1765426.1973 | 443121.9755 | 2029 | PADSTOW | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2028 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200966 | REP 210m CONSAC S004425_1 HOPE ST | 0.21 | 1765426.1973 | 370739.5014 | 2029 | PYMBLE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2028 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200968 | REP 207m CONSAC S004142_3 LINDEN AVE | 0.207 | 1765426.1973 | 365443.2228 | 2029 | PYMBLE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2028 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200969 | REP 170m CONSAC S002734_1 JOSEPH ST NORT | 0.17 | 1765426.1973 | 300122.4535 | 2029 | LIDCOMBE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2028 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.05 | LV Consac Cables (km); | 1700200970 | REP 266m CONSAC S004387_2 EDWARD ST EAST | 0.266 | 1765426.1973 | 469603.3685 | 2029 | RYDE | Ausgrid has approximately 890 kilometres of CONSAC cable that was installed between late 1960 and early 1990s. These cables are experiencing premature condition issues due to sheath corrosion and degradation of the paper insulation as a result of moisture ingress. Degradation of the cable paper insulation will typically result in a breakdown failure resulting in a supply interruption. The magnitude of this depends on the location, length, number of customers connected and duration of the associated outage. The need to replace CONSAC cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all CONSAC cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents.
REP_04.02.06 | Low Voltage HDPE Cables (km) | 1700245584 | REP 182m HDPE S001191_1 NO11 CHURCHILL S | 0.182 | 1568304.006 | 285431.3291 | 2026 | SILVERWATER | Ausgrid has approximately 110km of LV HDPE cable installed on its distribution network, which was installed between the mid 1970s until the mid 1980s. Ausgrid's HDPE LV cables have higher failure rates than other types of LV cable on the network. The need to replace HDPE cables has been triggered by condition related issues which have resulted in; • safety risks to the public, customers and workers due to uncontrolled discharge of electricity or loss of the electricity supply neutral connection, and • network reliability risks due to their high failure rate leading to a significant number of interruptions to the electricity supply to customers. Ausgrid has developed a prioritised planned replacement program of all HDPE cable distributors to mitigate these risks. The priorities are revised as new information becomes available through cable testing (e.g IR or sheath testing), breakdowns and investigations as a result of customer complaints or safety incidents. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.12 | LV Metallic Sheathed Cables (km) | 1700520059 | REP 148m Met Sheath Cable S008117_4 Macq | 0.148 | 1400693.1492 | 207302.5861 | 2026 | SYDNEY | Ausgrid has approximately 785km of Low Voltage underground metallic sheathed cable which supply electricity from distribution substations to customers. LV metallic sheathed cable failures can result in consequences including safety risks, fire risk, unserved energy and other risks. A planned replacement strategy has been adopted for the replacement of LV metallic sheathed cable based on a detailed risk assessment.
REP_04.02.12 | LV Metallic Sheathed Cables (km) | 1700520064 | REP 171m Met Sheath Cable S003750_5 King | 0.172 | 1400693.1492 | 240919.2217 | 2026 | SYDNEY | Ausgrid has approximately 785km of Low Voltage underground metallic sheathed cable which supply electricity from distribution substations to customers. LV metallic sheathed cable failures can result in consequences including safety risks, fire risk, unserved energy and other risks. A planned replacement strategy has been adopted for the replacement of LV metallic sheathed cable based on a detailed risk assessment. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_04.02.12 | LV Metallic Sheathed Cables (km) | 1700520067 | REP 196m Met Sheath Cable S006703_4 Fitz | 0.197 | 1400693.1492 | 275936.5504 | 2026 | MARRICKVILLE | Ausgrid has approximately 785km of Low Voltage underground metallic sheathed cable which supply electricity from distribution substations to customers. LV metallic sheathed cable failures can result in consequences including safety risks, fire risk, unserved energy and other risks. A planned replacement strategy has been adopted for the replacement of LV metallic sheathed cable based on a detailed risk assessment. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700681449 | TRANSMISSION FEEDER & TOWER RECOVERY | 1 | 363033.1131 | 363033.1131 | 2026 |  | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700354217 | REP TOWER 25C LE35910 FDR 910/911 | 1 | 363033.1131 | 363033.1131 | 2026 | CANTERBURY | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700795506 | REP TOWER FF00511 9M1-9M2-043 | 1 | 363033.1131 | 363033.1131 | 2026 | FRENCHS FOREST | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2025 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700379143 | REP TOWER 952-001 FDR 95A | 1 | 363033.1131 | 363033.1131 | 2026 | KILLINGWORTH | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2026 | No Change
REP_05.02.01-5 | Tower Replacement | 1700440038 | REP TWR REPLACEMENT PRIORITY DESIGN | 1 | 363033.1131 | 363033.1131 | 2027 |  | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700550482 | REP COMMS TOWER STRUCTURAL Black mntn | 1 | 363033.1131 | 363033.1131 | 2027 | Wingen | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2026 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700642438 | REP TOWER KL488 FDR 916/917 | 1 | 363033.1131 | 363033.1131 | 2027 | KURNELL | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2027 | No Change
REP_05.02.01-5 | Tower Replacement | 1700642435 | REP TOWER KL487 FDR 916/917 | 1 | 363033.1131 | 363033.1131 | 2027 | KURNELL | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2027 | No Change
REP_05.02.01-5 | Tower Replacement | 1700642422 | REP TOWER KL486 FDR 916/917 | 1 | 363033.1131 | 363033.1131 | 2027 | KURNELL | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2027 | No Change
REP_05.02.01-5 | Tower Replacement | 1700642416 | REP TOWER KL485 FDR 916/917 | 1 | 363033.1131 | 363033.1131 | 2028 | KURNELL | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700642436 | REP TOWER KL484 FDR 916/917 | 1 | 363033.1131 | 363033.1131 | 2028 | KURNELL | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2027 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700642425 | REP TOWER KL489 FDR 916/917 | 1 | 363033.1131 | 363033.1131 | 2028 | KURNELL | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2028 | No Change
REP_05.02.01-5 | Tower Replacement | 1700642433 | REP TOWER CR9147 FDR 916/917 | 1 | 363033.1131 | 363033.1131 | 2028 | KURNELL | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2028 | No Change
REP_05.02.01-5 | Tower Replacement | 1700642440 | REP TOWER CR9148 FDR 916/917 | 1 | 363033.1131 | 363033.1131 | 2028 | KURNELL | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2028 | No Change
REP_05.02.01-5 | Tower Replacement | 1700642443 | REP TOWER CR9145 FDR 916/917 | 1 | 363033.1131 | 363033.1131 | 2029 | KURNELL | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2028 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700642442 | REP TOWER CR9144 FDR 916/917 | 1 | 363033.1131 | 363033.1131 | 2029 | KURNELL | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option. | 2028 | Work has been reprioritised based on condition and risk assessment and available resources.
REP_05.02.01-5 | Tower Replacement | 1700642444 | REP TOWER CR9143 FDR 916/917 | 1 | 363033.1131 | 363033.1131 | 2029 | KURNELL | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option.
REP_05.02.01-5 | Tower Replacement | 1700642446 | REP TOWER CR9142 FDR 916/917 | 1 | 363033.1131 | 363033.1131 | 2029 | KURNELL | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option.
REP_05.02.01-5 | Tower Replacement | 1700642445 | REP TOWER CR9141 FDR 916/917 | 1 | 363033.1131 | 363033.1131 | 2029 | KURNELL | The need for the replacement of these assets is driven by the consequences of failure which include tower failure or inability to support overhead conductors at the required clearances. Ausgrid uses condition assessment data to determine refurbishment requirements or replacement timing. Cost-benefit analysis has been undertaken to determine the most cost effective option to manage the risk. This analysis compares refurbishment and replacement options on a case by case basis. Replacement with poles has been found to be the most cost effective replacement option.