## Tech Specs - (ZS)
Technical Specifications - Zone Substation
Name | Voltage Level | Area Plan | Summer | [5 empty] | Winter
|  |  | Total Capacity (MVA) | Firm Capacity (MVA) | Load Transfer Capacity (MVA) | 95% Peak Load Exceeded (hrs/yr) | Embedded Generation - Solar PV (MW) | Embedded Generation - Other (MW) | Total Capacity (MVA) | Firm Capacity (MVA) | Load Transfer Capacity (MVA) | 95% Peak Load Exceeded (hrs/yr) | Embedded Generation - Solar PV (MW) | Embedded Generation - Other (MW)
ABERDEEN | 66/11kV | Upper Hunter | 46.4 | 25.5 | 5.5 | 3.5 | 2.44 | 0 | 46.4 | 25.5 | 4.3 |  | 2.56 | 0
ADAMSTOWN | 132/11kV | Newcastle | 125.2 | 63 | 17.8 | 1.8 | 10.46 | 0.19 | 130 | 65 | 13.9 |  | 11.53 | 0.19
ARGENTON | 132/11kV | Newcastle Western Corridor | 121.4 | 60.8 | 22.1 | 1.5 | 15.36 | 0.09 | 121.4 | 64.2 | 15 |  | 16.23 | 0.09
AUBURN | 33/11kV | Auburn/Homebush | 75.9 | 30.6 | 18.8 | 3.5 | 3.73 | 0 | 75.9 | 41 | 14.7 |  | 3.88 | 0
AVOCA | 66/11kV | Lower Central Coast | 97.9 | 59.8 | 19.2 | 1.5 | 16.68 | 1.02 | 101.8 | 63.7 | 15.5 |  | 18.4 | 1.02
AVONDALE | 33/11kV | West Lake Macquarie | 47.2 | 23.6 | 9.6 | 1.5 | 8.37 | 0 | 47.2 | 23.6 | 6.5 |  | 9 | 0
BAERAMI | 33/11kV | Upper Hunter | 2.4 | 0 | 0 | 1.8 | 0.21 | 0 | 2.7 | 0 | 0 | 1 | 0.25 | 0
BALGOWLAH NORTH | 132/11kV | Manly Warringah | 76.5 | 43.9 | 17.5 | 1.3 | 12.34 | 0.01 | 76.5 | 43.9 | 17.2 | 6.5 | 13.46 | 0.01
BANKSTOWN | 132/11kV | Canterbury Bankstown | 127.7 | 63.5 | 28.6 | 2 | 14.25 | 0 | 128.2 | 65 | 22 |  | 15.03 | 0.2
BASS HILL | 33/11kV | Canterbury Bankstown | 40.1 | 20.7 | 0.6 | 2.8 | 4.74 | 0 | 40.1 | 20.7 | 0.4 |  | 5.24 | 0
BEACON HILL | 33/11kV | Manly Warringah | 54.1 | 26.7 | 18.6 |  | 6.01 | 0 | 54.1 | 26.7 | 16.8 | 3.3 | 7.25 | 0
BELMORE PARK | 132/11kV | Sydney CBD | 231.49 | 125.6 | 0 | 22.5 | 0.34 | 1.28 | 231.49 | 125.6 | 0 |  | 0.34 | 1.28
BELROSE | 33/11kV | Manly Warringah | 70.5 | 40.3 | 12.2 | 2 | 11.57 | 0 | 70.5 | 44.3 | 10.3 |  | 12.81 | 0
BERKELEY VALE | 132/11kV | Lower Central Coast | 117.6 | 59.9 | 20.1 | 6 | 14.21 | 0 | 117.6 | 63.3 | 16.3 |  | 15.56 | 0
BEROWRA | 132/11kV | North West | 82.9 | 42.3 | 8.8 | 1.8 | 10.69 | 0 | 85.5 | 44.6 | 8.1 | 0.3 | 11.62 | 0
BLACKWATTLE BAY | 33/5kV | Camperdown and Blackwattle Bay |  |  |  | 0.8 | 0 | 0 |  |  |  |  | 0 | 0
BLAKEHURST | 33/11kV | St George | 47.4 | 31.6 | 12.3 | 3.5 | 7.08 | 0 | 47.4 | 31.6 | 11.8 | 2.8 | 7.79 | 0
BOTANY | 33/11kV | Eastern Suburbs | 89 | 55.2 | 17.4 | 2.3 | 5.39 | 0 | 89 | 55.2 | 14.9 |  | 6 | 0
BRANDY HILL | 132/11kV | Maitland | 76.2 | 38.1 | 2.6 | 2 | 5.79 | 0 | 76.2 | 38.1 | 1.5 |  | 6.21 | 0
BRANXTON | 66/11kV | Singleton | 28.9 | 15.1 | 6.4 | 2.8 | 9.78 | 0.01 | 31.8 | 16.3 | 4.3 |  | 10.62 | 0.01
BROADMEADOW | 132/11kV | Newcastle Inner City | 109.4 | 59.5 | 21.5 | 5.3 | 7.74 | 0 | 109.4 | 59.5 | 18.4 |  | 8.85 | 0
BROOKVALE | 33/11kV | Manly Warringah | 88.8 | 55.1 | 25.9 | 2 | 6.29 | 0 | 88.8 | 55.1 | 21 |  | 6.74 | 0
BURWOOD | 132/11kV | Auburn/Homebush | 152.4 | 89.4 | 34.9 | 3.3 | 12.3 | 0 | 152.4 | 96.2 | 25.1 |  | 13.13 | 0
CAMPBELL ST | 132/11kV | Eastern Suburbs | 127 | 62.8 | 34.8 | 6 | 1.23 | 0.01 | 127 | 65 | 25.8 |  | 1.28 | 0.01
CAMPERDOWN | 33/11kV | Camperdown and Blackwattle Bay |  | 58.3 | 21.8 | 3.8 | 1.99 | 0 |  | 58.3 | 15.7 |  | 2.13 | 0
CAMPERDOWN | 33/5kV | Camperdown and Blackwattle Bay | 27.7 | 13.9 | 0 | 10 | 0 | 0 | 27.7 | 13.9 | 0 | 0.3 | 0 | 0
CAMPSIE | 33/11kV | Canterbury Bankstown | 140.6 | 87 | 24.9 | 2.5 | 15.51 | 0 | 140.6 | 87 | 21.5 |  | 17.01 | 0
CARDIFF | 33/11kV | Newcastle Western Corridor | 45.7 | 22.9 | 10.6 | 1.5 | 9.3 | 0 | 45.7 | 22.9 | 7.1 |  | 9.99 | 0
CAREEL BAY | 33/11kV | Pittwater and Terrey Hills | 23.4 | 19.7 | 5.5 |  | 4.35 | 0 | 23.4 | 21.7 | 5.7 | 2.3 | 4.94 | 0
CARINGBAH | 33/11kV | Sutherland | 76.2 | 38.1 | 22.5 | 3.8 | 3.95 | 0 | 76.2 | 38.1 | 19.3 |  | 4.45 | 0
CASTLE COVE | 132/11kV | Lower North Shore | 152.4 | 90.7 | 34.9 | 2.3 | 11.53 | 0 | 152.4 | 96.3 | 25.2 |  | 12.57 | 0
CESSNOCK SOUTH | 33/11kV | Greater Cessnock | 57 | 28.5 | 7.6 | 4.5 | 13.09 | 0 | 61.7 | 30.9 | 4.5 |  | 13.96 | 0
CHARLESTOWN | 132/11kV | North East Lake Macquarie | 113 | 60.2 | 32.8 | 2 | 11.64 | 0.02 | 113 | 60.2 | 25.1 |  | 12.52 | 0.02
CHARMHAVEN | 132/11kV | Upper Central Coast | 125.9 | 63.3 | 15.1 | 3.5 | 27.44 | 0 | 130 | 65 | 10.9 |  | 28.94 | 0
CHATSWOOD | 33/11kV | Lower North Shore | 121.9 | 67.1 | 33.8 |  | 9.1 | 0.1 | 122.1 | 70.5 | 26.8 | 10 | 9.9 | 0.1
CITY CENTRAL | 132/11kV | Sydney CBD | 254.35 | 128 | 0 | 50.3 | 0.13 | 5 | 254.35 | 130 | 0 |  | 0.13 | 6
CITY EAST | 33/11kV | Sydney CBD |  | 70.7 | 0 | 8 | 0 | 0 |  | 75.6 | 0 |  | 0 | 0
CITY NORTH | 132/11kV | Sydney CBD | 208.24 | 167.9 | 0 | 30 | 0.7 | 1.8 | 208.24 | 167.9 | 0 |  | 0.7 | 1.8
CITY SOUTH | 132/11kV | Sydney CBD | 199.98 | 130.3 | 0 | 35.3 | 0.23 | 0.77 | 199.98 | 130.3 | 0 |  | 0.25 | 0.77
CLOVELLY | 132/11kV | Eastern Suburbs | 96.4 | 43.8 | 33 | 0.3 | 5.6 | 0 | 103.7 | 46.5 | 36.4 | 12.3 | 6.06 | 0
CONCORD | 33/11kV | Auburn/Homebush | 81.4 | 54.4 | 14 | 2.5 | 7.06 | 0 | 81.4 | 54.4 | 8.8 |  | 7.58 | 0
CRONULLA | 132/11kV | Sutherland | 106.9 | 53.5 | 22.1 | 2.3 | 17.26 | 0.81 | 118.2 | 64.2 | 22.4 | 2 | 19.01 | 0.81
CROUDACE BAY | 33/11kV | North East Lake Macquarie | 74.9 | 38.1 | 15.9 | 1.5 | 10.46 | 0 | 76.2 | 38.1 | 9.9 |  | 11.25 | 0
CROWS NEST | 132/11kV | Lower North Shore | 123.8 | 61.6 | 30.7 | 4.5 | 3.68 | 0 | 123.8 | 65 | 29 | 5.3 | 3.97 | 0
CROYDON | 132/11kV | Auburn/Homebush | 126.5 | 62.6 | 24.4 | 1.5 | 9.2 | 0 | 130 | 65 | 25 | 7.5 | 9.68 | 0.36
DALLEY ST | 132/11kV | Sydney CBD | 243.22 | 123.6 | 0 | 22.8 | 0 | 4.2 | 258.01 | 130 | 0 |  | 0 | 4.2
DARLING HARBOUR | 132/11kV | Camperdown and Blackwattle Bay | 115.7 | 57.8 | 20.3 | 10.5 | 2.02 | 0 | 116.2 | 62 | 16.9 |  | 2.14 | 0
DARLINGHURST | 33/11kV | Eastern Suburbs | 118 | 80.6 | 15.8 | 8.8 | 0.48 | 0.49 | 123.7 | 84.8 | 12.5 |  | 0.49 | 0.49
DEE WHY WEST | 33/11kV | Manly Warringah | 97.1 | 53.5 | 24.3 | 1.8 | 12.33 | 0.4 | 101.5 | 58.8 | 24.5 | 0.8 | 13.8 | 0.4
DENMAN | 66/11kV | Upper Hunter | 30.7 | 15.3 | 1.8 | 1 | 2.37 | 0.06 | 33 | 16.5 | 1.1 |  | 2.52 | 0.06
DOUBLE BAY | 132/11kV | Eastern Suburbs | 157.5 | 101.3 | 27.7 | 3.5 | 4.6 | 0 | 158.1 | 101.3 | 26.1 | 0.5 | 5.13 | 0
DRUMMOYNE | 132/11kV | Auburn/Homebush | 102.1 | 56.2 | 17.7 | 1.8 | 9.74 | 0 | 112.3 | 61.8 | 17.2 |  | 10.45 | 0
DULWICH HILL | 33/11kV | Canterbury Bankstown | 87.6 | 61.9 |  | 7.5 | 0 | 0 |  |  |  |  | 0 | 0
EDGEWORTH | 33/11kV | Newcastle Western Corridor | 45.7 | 22.9 | 7.2 | 1.3 | 15.91 | 0.51 | 45.7 | 22.9 | 4.5 |  | 17.08 | 0.51
EMPIRE BAY | 66/11kV | Lower Central Coast | 76.2 | 38.1 | 11.5 | 1.8 | 7.51 | 0 | 76.2 | 38.1 | 9.6 |  | 8.27 | 0
ENGADINE | 132/11kV | Sutherland | 114.2 | 59.8 | 5.8 |  | 13.11 | 0 | 125.6 | 68.6 | 6 | 5.3 | 14.41 | 0
EPPING | 66/11kV | Carlingford | 114.3 | 74.9 | 32.9 | 2.8 | 10.26 | 0.01 | 114.3 | 74.9 | 24.2 |  | 11.14 | 0.01
ERINA | 66/11kV | Lower Central Coast | 81.2 | 46.9 | 16 | 1.5 | 10.73 | 0.02 | 83.5 | 46.9 | 11 |  | 11.62 | 0.02
FLEMINGTON | 132/11kV | Auburn/Homebush | 76.2 | 45.9 | 20.1 | 2.5 | 8.2 | 0.53 | 76.2 | 45.9 | 15.9 |  | 8.43 | 0.53
GALSTON | 132/11kV | North West | 76.2 | 38.1 | 8.9 | 3 | 5.09 | 0 | 76.2 | 38.1 | 7.7 |  | 5.39 | 0
GATESHEAD | 33/11kV | North East Lake Macquarie | 44.4 | 24.1 | 13.7 | 2 | 7.18 | 1.37 | 44.4 | 24.4 | 12.4 |  | 7.66 | 1.37
GORE HILL | 33/11kV | Lower North Shore | 137.9 | 92.2 | 18.8 | 5 | 3.79 | 0 | 139 | 92.2 | 18.2 | 0.5 | 3.95 | 0
GREEN SQUARE | 132/11kV | Eastern Suburbs | 171.5 | 114.3 | 36.2 | 4 | 4.81 | 0 | 171.5 | 114.3 | 27.2 |  | 4.94 | 0
GREENACRE | 132/11kV | Canterbury Bankstown | 129 | 62.3 | 0 | 3 | 11.62 | 0 | 132.5 | 65 | 0 |  | 12.64 | 0
GREENACRE PARK | 132/11kV | Canterbury Bankstown |  |  |  |  | 0 | 0 |  |  |  | 2952 | 0 | 0
HARBORD | 33/11kV | Manly Warringah | 76.2 | 38.1 | 18.3 |  | 9.58 | 0 | 76.2 | 38.1 | 23.8 | 3.3 | 10.32 | 0
HOMEBUSH BAY | 132/11kV | Auburn/Homebush | 106.7 | 53.2 | 37 | 9.5 | 3.65 | 0 | 115.1 | 57.4 | 27.9 |  | 3.68 | 0
HORNSBY | 132/11kV | North West | 171.5 | 114.3 | 32.3 | 2.5 | 19.2 | 0.55 | 171.5 | 114.3 | 27.6 | 11 | 21.08 | 0.55
HUNTERS HILL | 66/11kV | Carlingford | 113.5 | 72.3 | 24.7 | 2.3 | 13.84 | 0 | 113.5 | 72.3 | 19.2 |  | 15.42 | 0
HURSTVILLE NORTH | 132/11kV | St George | 109.3 | 59.6 | 20.6 | 2.5 | 7.12 | 0 | 109.3 | 59.6 | 15.6 |  | 7.62 | 0
JANNALI | 33/11kV | Sutherland | 61.3 | 38.1 | 14.6 | 2 | 12.61 | 0 | 62.7 | 38.1 | 14.4 |  | 13.93 | 0
JESMOND | 132/11kV | Newcastle Port | 107.5 | 57.5 | 32.5 | 1.8 | 15.07 | 0.64 | 107.5 | 57.5 | 24.7 |  | 16.99 | 0.64
JEWELLS | 33/11kV | North East Lake Macquarie | 30.8 | 16.9 | 12.7 | 1.5 | 8.11 | 0 | 32.5 | 18.1 | 10.9 |  | 8.67 | 0
KILLARNEY | 33/11kV | Manly Warringah | 21.1 | 21.1 | 9.7 | 1.8 | 6.43 | 0 | 21.1 | 21.1 | 8.8 |  | 7.26 | 0
KINGSFORD | 132/11kV | Eastern Suburbs | 124.6 | 62.2 | 31.4 | 0.3 | 9.82 | 5.77 | 124.6 | 65 | 33.2 | 9.8 | 10.69 | 5.77
KIRRAWEE | 132/11kV | Sutherland | 76.2 | 42.9 | 23.8 | 2.8 | 10.94 | 0.01 | 76.2 | 42.9 | 24.4 | 5.8 | 12.22 | 0.01
KOGARAH | 132/11kV | St George | 170.8 | 114.3 | 57.8 | 2.5 | 12.62 | 0 | 170.8 | 114.3 | 51 |  | 13.73 | 0
KOTARA | 33/11kV | Newcastle Inner City | 37.3 | 30.8 | 19.7 | 2 | 8.59 | 0 | 38.1 | 33.9 | 13.4 |  | 9.21 | 0
KURNELL SOUTH | 132/11kV | Sutherland | 76.2 | 38.1 | 0.4 | 0.8 | 2.39 | 0 | 76.2 | 38.1 | 0.4 | 2.8 | 2.46 | 0
KURRI | 132/11kV | Greater Cessnock | 104.2 | 57.3 | 0 | 2.3 | 17.69 | 0.26 | 104.2 | 57.3 | 0 |  | 19 | 0.27
LAKE MUNMORAH | 132/11kV | Upper Central Coast | 76.2 | 38.1 | 7.5 | 1.3 | 12.92 | 0 | 76.2 | 38.1 | 5.7 |  | 13.92 | 0
LEICHHARDT | 132/11kV | Auburn/Homebush | 109.3 | 59.5 | 19.1 | 0.5 | 7.43 | 0 | 120.3 | 62.5 | 20.2 | 6.5 | 7.93 | 0
LEIGHTONFIELD | 33/11kV | Canterbury Bankstown | 38.4 | 22.9 | 11.6 | 5 | 5.15 | 0 | 38.4 | 22.9 | 10.3 |  | 5.54 | 0
LIDCOMBE | 33/11kV | Auburn/Homebush | 54.1 | 33.4 | 4.7 | 3.5 | 3.77 | 0 | 55.2 | 33.4 | 3.2 |  | 6.92 | 0
LINDFIELD | 33/11kV | Upper North Shore | 66.3 | 36.8 | 16 | 0.5 | 10.72 | 0 | 73 | 40.5 | 15.1 | 7 | 11.82 | 0
LISAROW | 33/11kV | Lower Central Coast | 47.6 | 23.8 | 7.3 | 1.5 | 9.41 | 0 | 47.6 | 23.8 | 5.8 |  | 10.61 | 0
LONG JETTY | 66/11kV | Lower Central Coast | 114.3 | 71.7 | 0 | 0.8 | 21.04 | 0 | 114.3 | 76.2 | 0 |  | 22.57 | 0
MACQUARIE PARK | 132/11kV | Carlingford | 171.5 | 114.3 | 23.4 | 32.8 | 3.41 | 1.52 | 171.5 | 114.3 | 17 |  | 3.67 | 1.52
MAITLAND | 33/11kV | Maitland | 73.3 | 36.7 | 4.3 | 1.8 | 11.24 | 0.02 | 74.3 | 38.1 | 2.4 |  | 11.95 | 0.02
MANLY | 33/11kV | Manly Warringah | 45.7 | 22.9 | 16 |  | 2.34 | 0.01 | 45.7 | 22.9 | 17.4 | 6.5 | 2.48 | 0.01
MAROUBRA | 132/11kV | Eastern Suburbs | 150.6 | 102.8 | 13.4 | 4.8 | 7.51 | 0.34 | 150.6 | 102.8 | 14.4 | 14 | 8.23 | 0.34
MARRICKVILLE | 132/11kV | Eastern Suburbs | 76.2 | 71.9 | 27.8 | 1 | 13.58 | 0.01 | 76.4 | 72.7 | 29.7 | 8 | 14.73 | 0.01
MARYLAND | 132/11kV | Newcastle Western Corridor | 76.2 | 38.1 | 8.9 | 1 | 21 | 4.68 | 76.2 | 38.1 | 4.6 |  | 22.8 | 4.68
MASCOT | 33/11kV | Eastern Suburbs | 103.6 | 78.4 | 24.9 | 4 | 2.14 | 0 | 105.1 | 81.9 | 18.6 |  | 2.35 | 0
MAYFIELD WEST | 132/11kV | Newcastle Port | 126.4 | 62.6 | 8.3 | 2.3 | 7 | 6.81 | 126.4 | 65 | 7.3 |  | 7.39 | 6.81
MEADOWBANK | 132/11kV | Carlingford | 152.8 | 103.8 | 31.8 | 4.3 | 14.33 | 0.02 | 157.7 | 108.7 | 23.6 |  | 15.56 | 0.02
MEDOWIE | 33/11kV | Port Stephens | 73 | 38.1 | 6.7 | 1.3 | 11.31 | 0 | 73 | 38.1 | 4.9 |  | 12.4 | 0
MENAI | 132/11kV | Sutherland | 121.4 | 60.7 | 10.8 | 2 | 20.22 | 0.02 | 130 | 65 | 8 |  | 22.07 | 0.02
MERRIWA | 33/11kV | Upper Hunter | 6.9 |  | 0 | 2.8 | 1.55 | 0.02 | 7.6 |  | 0 |  | 1.61 | 0.02
METFORD | 33/11kV | Maitland | 79 | 41.6 | 21.8 | 3 | 19.95 | 2.1 | 79 | 41.6 | 15.4 |  | 21.46 | 2.1
MILPERRA | 132/11kV | Canterbury Bankstown | 123.2 | 61.2 | 22.2 | 2 | 13.51 | 0 | 123.2 | 64.6 | 18.1 |  | 14.41 | 0
MIRANDA | 33/11kV | Sutherland | 71.9 | 42 | 23 | 1.5 | 7.15 | 0.01 | 71.9 | 42 | 19.9 |  | 7.96 | 0.01
MITCHELL LINE | 66/11kV | Upper Hunter | 47.6 | 23.8 | 9 | 1 | 3.38 | 0 | 47.6 | 23.8 | 7 | 0.5 | 3.69 | 0
MITCHELLS FLAT | 66/11kV | Singleton | 6.7 |  | 0 | 1.5 | 1.1 | 0 | 6.7 |  | 0 |  | 1.21 | 0
MONA VALE | 33/11kV | Pittwater and Terrey Hills | 104.6 | 57.4 | 12.5 | 1.8 | 11.09 | 1.04 | 105.4 | 59.6 | 11.4 |  | 12.31 | 1.04
MOONAN | 33/11kV | Upper Hunter | 6.9 | 2.9 | 0 |  | 0.23 | 0 | 7.6 | 3.1 | 0 | 1.5 | 0.24 | 0
MORISSET | 132/11kV | West Lake Macquarie | 76.2 | 38.1 | 10 | 1.8 | 16.54 | 1.6 | 76.2 | 38.1 | 7.3 |  | 17.65 | 1.6
MORTDALE | 33/11kV | West Lake Macquarie | 114.3 | 64.3 | 21.3 | 1.8 | 15.51 | 0 | 114.3 | 70.7 | 18.2 |  | 16.93 | 0
MOSMAN | 132/11kV | West Lake Macquarie | 152.4 | 82.5 | 24 | 0.8 | 12.25 | 0.17 | 152.4 | 89.1 | 25.9 | 6.8 | 13.55 | 0.17
MOUNT HUTTON | 33/11kV | North East Lake Macquarie | 52 | 26 | 19.8 | 1.3 | 8.88 | 0 | 52 | 26 | 13.3 |  | 9.76 | 0
MUSWELLBROOK | 33/11kV | Upper Hunter | 47.6 | 23.8 | 9.3 | 2.5 | 6.32 | 0.2 | 47.6 | 23.8 | 6.6 |  | 6.74 | 0.2
NARRABEEN | 33/11kV | Pittwater and Terrey Hills | 20.3 | 19.6 | 12.7 | 2 | 5.56 | 0 | 20.3 | 21.1 | 12.3 |  | 5.94 | 0
NELSON BAY | 33/11kV | Port Stephens | 65.6 | 45.7 | 16.5 | 1.3 | 13.38 | 0 | 68.6 | 45.7 | 15.3 |  | 14.72 | 0
NEW LAMBTON | 33/11kV | Newcastle Inner City | 44.4 | 23.6 | 7.8 | 2 | 4.73 | 0.01 | 47.2 | 23.6 | 4.5 |  | 5.08 | 0.01
NEWCASTLE CBD | 33/11kV | Newcastle Inner City | 112.8 | 76.2 | 22.6 | 4.8 | 7.69 | 0 | 112.8 | 76.2 | 16.4 |  | 8.4 | 0
NEWPORT | 33/11kV | Pittwater and Terrey Hills | 22.6 | 20.8 | 12 |  | 5.01 | 0 | 22.6 | 22.4 | 14.2 | 2 | 5.62 | 0
NORAVILLE | 33/11kV | Upper Central Coast | 45.2 | 30.1 | 13.8 | 1.8 | 12.35 | 0.01 | 45.2 | 30.1 | 11.8 |  | 13.31 | 0.01
NORTH HEAD | 33/11kV | Manly Warringah | 44.8 | 23.4 | 5.5 | 13.5 | 0.85 | 2.1 | 44.8 | 29.2 | 3.9 |  | 0.94 | 2.1
NORTH SYDNEY | 132/11kV | Lower North Shore | 171.5 | 114.3 | 17.9 | 5.8 | 1.67 | 3.11 | 171.5 | 114.3 | 14.7 |  | 1.9 | 3.11
NULKABA | 33/11kV | Greater Cessnock | 76.2 | 38.1 | 9.8 | 5.5 | 11.18 | 0 | 76.2 | 38.1 | 6 |  | 11.55 | 0
OLYMPIC PARK | 132/11kV | Auburn/Homebush | 120.3 | 56.8 | 34.3 | 3.5 | 4.42 | 0.52 | 122.6 | 60 | 23 |  | 4.69 | 0.52
PADDINGTON | 33/11kV | Eastern Suburbs | 114.3 | 66.5 | 26.3 | 10.5 | 1.15 | 0 | 114.3 | 69.8 | 24.6 | 8.5 | 1.21 | 0
PAXTON | 33/11kV | Greater Cessnock | 25.5 |  | 0.1 | 2 | 5.1 | 0 | 25.5 |  | 0.1 |  | 5.42 | 0
PEATS RIDGE | 33/11kV | Lower Central Coast | 29.2 | 17.1 | 4.2 | 7.5 | 5.16 | 0.01 | 29.2 | 18.6 | 3.3 |  | 5.52 | 0.01
PELICAN | 33/11kV | North East Lake Macquarie | 49.6 | 25.6 | 7.3 | 1.5 | 4.52 | 0 | 51.3 | 25.6 | 7.3 |  | 4.9 | 0
PENNANT HILLS | 132/11kV | North West | 164.1 | 106.9 | 21.9 | 2 | 30.48 | 0.02 | 171.5 | 114.3 | 16.2 |  | 33.25 | 0.02
PORT BOTANY | 33/11kV | Eastern Suburbs | 112.3 | 59.2 | 10.7 | 2.8 | 0.87 | 0 | 112.3 | 59.2 | 10.4 |  | 1.21 | 0
POTTS HILL | 132/11kV | Canterbury Bankstown | 109.7 | 54.9 | 35.1 | 4 | 10.49 | 0.01 | 109.7 | 54.9 | 26.3 |  | 11.03 | 0.01
PUNCHBOWL | 33/11kV | Canterbury Bankstown | 87.2 | 60.8 | 17.2 | 3 | 9.74 | 0 | 91.7 | 63.8 | 13.7 |  | 10.49 | 0
PYMBLE | 33/11kV | Upper North Shore | 67.7 | 39.4 | 26.4 | 2.3 | 8.92 | 0 | 67.7 | 41.5 | 22.1 |  | 9.75 | 0
RATHMINES | 132/11kV | West Lake Macquarie | 76.2 | 38.1 | 4.3 | 1.3 | 9.44 | 0.85 | 76.2 | 38.1 | 3 |  | 10.02 | 0.89
RAYMOND TERRACE | 33/11kV | Port Stephens | 73.6 | 38.11 | 9 | 2 | 10.53 | 0 | 73.6 | 38.11 | 7.3 |  | 11.27 | 0
REVESBY | 132/11kV | Canterbury Bankstown | 76.2 | 44.9 | 12.9 | 1.8 | 15.85 | 0.02 | 76.2 | 47.8 | 10.6 |  | 17.62 | 0.02
RIVERWOOD | 33/11kV | St George | 65.7 | 42.8 | 20.7 | 1.8 | 9.97 | 0.01 | 65.7 | 42.8 | 18.8 |  | 10.9 | 0.01
ROCKDALE | 132/11kV | St George | 109.3 | 59.5 | 0 | 4.3 | 7.87 | 0 | 120.3 | 62.5 | 0 |  | 8.84 | 0
ROSE BAY | 132/11kV | Eastern Suburbs | 111.3 | 59.3 | 16.7 | 3 | 8.28 | 1.42 | 111.3 | 59.3 | 16.6 | 4 | 9.06 | 1.42
ROTHBURY | 132/11kV | Greater Cessnock | 76.2 | 38.1 | 6.2 | 4 | 7.17 | 0 | 76.2 | 38.1 | 3.7 |  | 7.96 | 0
ROUCHEL | 33/11kV | Upper Hunter | 5.8 |  | 1.4 |  | 0.26 | 0.01 | 6.3 |  | 1.1 | 0.3 | 0.26 | 0.01
RUTHERFORD | 33/11kV | Maitland | 76.2 | 38.1 | 3.4 | 3 | 16.3 | 0 | 76.2 | 38.1 | 2.5 |  | 17.59 | 0
SANS SOUCI | 33/11kV | St George | 48.6 | 24.3 | 8.9 | 2.8 | 4.53 | 0.01 | 48.6 | 24.3 | 8.1 |  | 5.01 | 0.01
SCONE | 66/11kV | Upper Hunter | 76.2 | 38.1 | 4.1 | 3.8 | 6.21 | 5.5 | 76.2 | 38.1 | 3.1 |  | 6.56 | 5.52
SEFTON | 132/11kV | Canterbury Bankstown | 152.4 | 94.6 | 35.8 | 2 | 17.37 | 0 | 152.4 | 99.7 | 26.4 |  | 18.61 | 0
SINGLETON | 66/11kV | Singleton | 58.2 | 29.8 | 12.2 | 5.3 | 6.2 | 0 | 58.2 | 32 | 8.3 |  | 6.71 | 0
SINGLETON NORTH | 66/11kV | Singleton | 76.2 | 38.1 | 9 | 3 | 10.13 | 0 | 76.2 | 38.1 | 5.9 |  | 10.81 | 0
SOMERSBY | 132/11kV | Lower Central Coast | 104.5 | 51.9 | 6 |  | 10.3 | 0.65 | 112.3 | 56.1 | 6.8 | 0.8 | 10.86 | 0.65
ST IVES | 33/11kV | Upper North Shore | 101.4 | 58.5 | 18.9 | 2 | 16.86 | 0.01 | 108 | 63.7 | 16.7 | 1.3 | 18.65 | 0.01
ST PETERS | 132/11kV | Eastern Suburbs | 152.4 | 88.6 | 36.3 | 4 | 7.79 | 0.32 | 152.4 | 88.6 | 29.6 |  | 8.46 | 0.32
STOCKTON | 33/11kV | Port Stephens | 48.9 | 25.6 | 2.4 | 1 | 4.24 | 0 | 51.3 | 25.6 | 1.9 |  | 4.53 | 0
STRATHFIELD SOUTH | 132/11kV | Canterbury Bankstown | 134.8 | 67.3 | 0 | 3 | 7.88 | 0.03 | 135 | 67.5 | 0 |  | 8.43 | 0.03
SUMMER HILL | 33/11kV | Canterbury Bankstown | 101 | 71.1 | 0 | 3 | 9.98 | 0 | 100.9 | 61.7 | 0 |  | 10.77 | 0
SURRY HILLS | 33/11kV | Eastern Suburbs | 78.4 | 0 | 29.4 | 14.8 | 1.27 | 3.74 | 83.2 | 0 | 22.8 |  | 1.3 | 3.74
SWANSEA | 33/11kV | North East Lake Macquarie | 29.9 | 16.4 | 3.1 | 1.5 | 9.73 | 0.01 | 29.9 | 16.4 | 2.9 |  | 10.52 | 0.01
TANILBA BAY | 33/11kV | Port Stephens | 38.8 | 18.7 | 0.4 | 1.3 | 7.39 | 0 | 40.5 | 18.8 | 0.3 |  | 7.96 | 0
TARRO | 33/11kV | Maitland | 47.6 | 23.8 | 9.6 | 2.5 | 5.98 | 0 | 47.6 | 23.8 | 7.9 |  | 6.28 | 0
TELARAH | 33/11kV | Maitland | 28.9 | 15.2 | 6.9 | 2.8 | 8.55 | 0 | 30.5 | 15.2 | 3.7 |  | 9.1 | 0
TERREY HILLS | 33/11kV | Pittwater and Terrey Hills | 54 | 23.8 | 3.7 | 1.5 | 3.5 | 0 | 54 | 23.8 | 3.1 |  | 3.93 | 0
THORNTON | 33/11kV | Maitland | 110.9 | 61 | 10.9 | 1.5 | 20.55 | 0 | 114.3 | 67.1 | 6.7 |  | 22.42 | 0.02
TIGHES HILL | 33/11kV | Newcastle Inner City | 71.1 | 38.5 | 12.7 | 0.5 | 5.4 | 0 | 71.1 | 38.5 | 14.2 | 2 | 5.9 | 0
TOMAGO | 33/11kV | Port Stephens | 74.3 | 38.1 | 11.8 | 0.3 | 0 | 0 | 74.3 | 38.1 | 11.9 | 3.5 | 0 | 0
TOMALPIN | 33/11kV | Greater Cessnock | 20.8 |  | 0 |  | 2.25 | 0 | 22.2 |  | 0 | 1.3 | 2.33 | 0
TOMAREE | 33/11kV | Port Stephens | 73.3 | 38.1 | 0 | 1.5 | 8.02 | 0 | 73.3 | 38.1 | 0 | 1.3 | 8.68 | 0
TOP RYDE | 132/11kV | Carlingford | 113.3 | 61.3 | 0 | 3 | 11.38 | 0.01 | 113.3 | 61.3 | 0 |  | 12.31 | 0.01
TORONTO WEST | 132/11kV | West Lake Macquarie | 76.2 | 38.1 | 0 | 1.3 | 9.1 | 0.01 | 76.2 | 38.1 | 0 |  | 10.01 | 0.01
TURRAMURRA | 33/11kV | Upper North Shore | 72.5 | 42.3 | 0 |  | 10.55 | 0 | 73.6 | 44.3 | 0 | 5 | 11.72 | 0
UMINA | 66/11kV | Lower Central Coast | 71.4 | 35.7 | 0 | 2.3 | 11.71 | 1.01 | 75.7 | 37.9 | 0 |  | 12.79 | 1.01
VALES POINT | 33/11kV | Upper Central Coast | 30.5 | 15.2 | 0 | 1 | 0 | 0 | 30.5 | 15.2 | 0 | 3.3 | 0 | 0
WAMBERAL | 132/11kV | Lower Central Coast | 72.49 | 34.39 | 0 | 1.8 | 9.33 | 0.01 | 74.97 | 36.87 | 0 |  | 10.35 | 0.01
WAVERLEY | 132/11kV | Eastern Suburbs | 126 | 61.8 | 0 |  | 6.23 | 0.01 | 130 | 65 | 0 | 6.5 | 6.81 | 0.01
WEST GOSFORD | 132/11kV | Lower Central Coast | 130 | 65 | 0 | 2.8 | 14.39 | 0 | 130 | 65 | 0 |  | 15.46 | 0.02
WILLIAMTOWN | 33/11kV | Port Stephens | 48.1 | 25.6 | 0 | 1.8 | 2.84 | 0 | 51.3 | 25.6 | 0 | 1.3 | 2.99 | 0
WOY WOY | 66/11kV | Lower Central Coast | 62 | 30.8 | 0 |  | 7.82 | 0.01 | 68 | 32.7 | 0 | 3.3 | 8.55 | 0.01
WYONG | 132/11kV | Upper Central Coast | 110.3 | 54 | 0 | 3.5 | 24.56 | 2.23 | 115.2 | 58.8 | 0 |  | 26.23 | 2.23
ZETLAND | 132/11kV | Eastern Suburbs | 152.4 | 83.6 | 0 | 3.8 | 4.35 | 0 | 152.4 | 90.3 | 0 |  | 4.48 | 0
MATRAVILLE | 33/11kV | Eastern Suburbs | 86.8 | 57 | 31.9 | 0.3 | 9.47 | 2.94 | 88.9 | 58.5 | 33.9 | 9.3 | 10.26 | 2.94
RNS HOSPITAL | 132/11kV | Lower North Shore | 97.3 | 53.5 | 10.3 | 3.5 | 0.29 | 0 | 97.3 | 53.5 | 6.6 |  | 0.3 | 0
LEMINGTON | 66/11kV | Singleton | 22.6 | 6.7 | 1.3 | 0.3 | 0.41 | 0 | 24.5 | 6.7 | 1.1 |  | 0.42 | 0
MOUNT THORLEY | 66/11kV | Singleton | 35.2 | 20.3 | 2 | 4.3 | 4.73 | 0 | 35.2 | 20.3 | 1.5 | 1.5 | 4.88 | 0
NEWDELL | 66/11kV | Singleton | 47.6 | 23.8 | 3.7 | 1.5 | 0.14 | 0 | 47.6 | 23.8 | 3.6 | 1.3 | 0.16 | 0
GWAWLEY BAY | 132/11kV | Sutherland | 91.8 | 45.1 | 15.7 | 1 | 8.13 | 0 | 91.8 | 45.1 | 13 |  | 8.76 | 0
LUCAS HEIGHTS | 33/11kV | Sutherland | 38.5 | 19.2 | 0 | 11 | 0 | 0 | 44.1 | 22 | 0 |  | 0 | 0

## Actual Demand - (ZS)
Actual Demand - Zone Substation
Name | Summer | [5 empty] | Winter
| 2020/21 (MVA) | 2020/21 (PF) | 2021/22 (MVA) | 2021/22 (PF) | 2022/23 (MVA) | 2022/23 (PF) | 2021 (MVA) | 2023 (PF) | 2022 (MVA) | 2022 (PF) | 2023 (MVA) | 2023 (PF)
ABERDEEN | 5.3 | 1 | 3.8 | 1 | 4.6 | 1 | 3.6 | 1 | 3.6 | 0.99 | 4.3 | 1
ADAMSTOWN | 31.3 | 0.99 | 22.8 | 0.99 | 28.9 | 0.99 | 27.7 | 1 | 22.8 | 1 | 21.7 | 1
ARGENTON | 32.5 | 0.98 | 28.4 | 0.98 | 33.1 | 0.99 | 28.1 | 0.99 | 25.8 | 1 | 26 | 0.99
AUBURN | 26.3 | 0.96 | 28 | 0.97 | 25.1 | 0.94 | 22 | 0.98 | 19.4 | 0.98 | 21.2 | 0.95
AVOCA | 41.6 | 0.99 | 34 | 1 | 37.8 | 1 | 39.3 | 1 | 36.6 | 1 | 31.4 | 1
AVONDALE | 11 | 0.99 | 9 | 1 | 10.9 | 1 | 8.6 | 1 | 7.9 | 1 | 8.3 | 1
BAERAMI | 0.7 | 0.94 | 0.6 | 0.95 | 0.6 | 0.95 | 0.6 | 0.97 | 0.5 | 0.99 | 0.6 | 0.97
BALGOWLAH NORTH | 32 | 0.99 | 24.2 | 1 | 28.7 | 1 | 35.4 | 1 | 31.4 | 1 | 28.5 | 1
BANKSTOWN | 41.2 | 0.99 | 46.8 | 0.98 | 43.1 | 0.99 | 40.2 | 1 | 39.3 | 1 | 36.4 | 1
BASS HILL | 18.7 | 0.99 | 18.7 | 0.99 | 17.5 | 1 | 16.8 | 1 | 14.9 | 1 | 14.5 | 1
BEACON HILL | 19.1 | 0.94 | 20.5 | 0.94 | 17.2 | 0.94 | 21.1 | 0.9 | 18.5 | 0.96 | 18.5 | 0.96
BELMORE PARK |  |  | 11.1 | 0.97 | 20.4 | 0.98 |  |  | 14.1 | 0.9 | 17.1 | 0.9
BELROSE | 32.9 | 0.96 | 24.4 | 0.96 | 27.8 | 0.97 | 28 | 0.96 | 26.9 | 0.96 | 24 | 0.96
BERKELEY VALE | 41.6 | 0.99 | 41 | 0.98 | 40.3 | 0.98 | 35.8 | 0.99 | 35.8 | 1 | 34.6 | 0.99
BEROWRA | 20.4 | 0.94 | 20.7 | 0.92 | 22.6 | 0.93 | 24.5 | 0.97 | 22.3 | 0.97 | 21.6 | 0.97
BLACKWATTLE BAY | 5.8 | 0.89 | 2.1 | 0.94 | 0 |  | 3.3 | 0.94 | 1.1 | 0.94 | 0
BLAKEHURST | 22 | 0.97 | 20.7 | 0.99 | 22.1 | 0.98 | 21 | 0.96 | 22 | 0.95 | 21.8 | 0.95
BOTANY | 25.3 | 0.96 | 26.7 | 0.97 | 29.1 | 0.99 | 22.4 | 0.99 | 23.7 | 0.99 | 24.4 | 1
BRANDY HILL | 11.4 | 0.99 | 9.6 | 0.99 | 9.8 | 1 | 6.3 | 1 | 7.4 | 1 | 6.8 | 1
BRANXTON | 14.6 | 0.99 | 12.3 | 0.99 | 13.9 | 1 | 12 | 1 | 10.5 | 1 | 10.4 | 1
BROADMEADOW | 22.5 | 0.99 | 23.8 | 0.98 | 23.8 | 0.99 | 21.2 | 0.99 | 20 | 0.99 | 20.1 | 0.99
BROOKVALE | 37 | 0.98 | 40.4 | 0.94 | 37.9 | 0.94 | 36.1 | 0.99 | 37.5 | 0.98 | 31.6 | 0.98
BURWOOD | 68.2 | 0.99 | 72.1 | 0.99 | 67.4 | 0.96 | 62.8 | 1 | 58.1 | 0.99 | 55.7 | 0.96
CAMPBELL ST | 31.5 | 0.98 | 31.9 | 0.98 | 36.4 | 0.97 | 28.9 | 0.99 | 28.6 | 1 | 28.9 | 0.99
CAMPERDOWN | 26.7 | 0.99 | 23.2 | 1 | 28.8 | 1 | 23.9 | 1 | 20.7 | 1 | 21.6 | 1
CAMPERDOWN | 2.5 | 0.92 | 3.4 | 0.92 | 2.6 | 0.92 | 2.8 | 0.95 | 3.6 | 0.95 | 2.5 | 0.95
CAMPSIE | 68.1 | 0.97 | 66.9 | 0.97 | 66.7 | 0.99 | 67.8 | 0.99 | 65 | 0.99 | 61.9 | 0.99
CARDIFF | 24.1 | 0.98 | 14.9 | 0.99 | 18.9 | 0.99 | 15.5 | 1 | 14.3 | 1 | 14.2 | 1
CAREEL BAY | 12.2 | 1 | 9.4 | 0.99 | 10.6 | 0.99 | 13.6 | 0.99 | 11.8 | 0.99 | 11.5 | 0.99
CARINGBAH | 19.7 | 0.93 | 23.8 | 0.93 | 25 | 0.93 | 21.6 | 0.93 | 21.2 | 0.93 | 21.2 | 0.92
CASTLE COVE | 55.9 | 0.76 | 60.8 | 0.9 | 61.8 | 0.92 | 53.4 | 0.9 | 51.4 | 0.69 | 47.7 | 0.68
CESSNOCK SOUTH | 28.9 | 0.99 | 19.7 | 0.99 | 22.7 | 0.99 | 18.9 | 1 | 17.2 | 1 | 17.6 | 1
CHARLESTOWN | 32.8 | 0.99 | 28.2 | 0.99 | 32.5 | 0.99 | 30.2 | 1 | 26 | 1 | 24.8 | 1
CHARMHAVEN | 47.9 | 0.99 | 42.6 | 0.99 | 42.3 | 1 | 37.9 | 1 | 34.9 | 1 | 34.8 | 1
CHATSWOOD | 41.9 | 0.92 | 39.8 | 0.91 | 32.6 | 0.92 | 42.6 | 0.94 | 43.4 | 0.94 | 38.6 | 0.95
CITY CENTRAL | 84.2 | 0.93 | 82 | 0.95 | 87.5 | 0.91 | 65.4 | 0.95 | 66.7 | 0.95 | 74.3 | 0.95
CITY EAST | 29 | 0.97 | 25.4 | 0.99 | 13.5 | 0.98 | 21.7 | 0.97 | 14.3 | 0.98 | 0
CITY NORTH | 90.1 | 0.95 | 89.3 | 0.94 | 95.4 | 0.95 | 71.9 | 0.97 | 70 | 0.66 | 70.9 | 0.66
CITY SOUTH | 92.3 | 0.95 | 93.8 | 0.95 | 98.5 | 0.95 | 73.7 | 0.95 | 74.9 | 0.95 | 72.2 | 0.95
CLOVELLY | 35.3 | 0.99 | 33.8 | 0.99 | 36.2 | 1 | 42.9 | 1 | 41.2 | 1 | 38 | 1
CONCORD | 38.3 | 0.96 | 42.4 | 0.96 | 40 | 0.96 | 34.1 | 0.98 | 31.3 | 0.98 | 30.5 | 0.98
CRONULLA | 55.7 | 0.98 | 51.5 | 0.98 | 54 | 0.98 | 60.7 | 0.99 | 56 | 0.99 | 52.3 | 0.99
CROUDACE BAY | 25.4 | 0.74 | 18.2 | 0.98 | 23.2 | 0.99 | 16.5 | 1 | 14.3 | 1 | 13.8 | 1
CROWS NEST | 34.8 | 0.99 | 39.6 | 1 | 35.8 | 0.9 | 38.2 | 1 | 33.4 | 0.96 | 35.2 | 0.9
CROYDON | 32.8 | 1 | 34.5 | 1 | 33.3 | 0.99 | 38.7 | 1 | 35.2 | 0.99 | 33.6 | 0.99
DALLEY ST | 35.1 | 0.98 | 36.2 | 0.99 | 35.8 | 0.95 | 28.4 | 0.99 | 28.7 | 0.96 | 22.4 | 0.96
DARLING HARBOUR | 50.4 | 0.98 | 55.9 | 0.98 | 48.9 | 0.98 | 45.3 | 1 | 45.8 | 1 | 42 | 1
DARLINGHURST | 37.2 | 0.98 | 37.9 | 0.98 | 39.9 | 0.98 | 35.2 | 0.99 | 33.1 | 1 | 33.1 | 1
DEE WHY WEST | 37.3 | 0.93 | 32.1 | 0.93 | 41.2 | 0.93 | 44.3 | 0.98 | 43.1 | 0.98 | 39.5 | 0.98
DENMAN | 5.4 | 0.99 | 4.1 | 0.99 | 5 | 0.99 | 3.5 | 1 | 3.5 | 1 | 3.9 | 1
DOUBLE BAY | 55.5 | 0.98 | 54.2 | 0.98 | 55.1 | 0.93 | 61.6 | 0.99 | 56.1 | 1 | 52.9 | 1
DRUMMOYNE | 51.5 | 0.99 | 51.1 | 0.97 | 55.1 | 0.97 | 59.6 | 0.98 | 56.3 | 0.98 | 52.4 | 0.98
DULWICH HILL | 40.7 | 0.98 | 39.5 | 0.98 | 0 |  | 46.8 | 0.98 | 44.8 | 0.98 | 0
EDGEWORTH | 27.5 | 0.99 | 21.1 | 1 | 26.2 | 0.99 | 20.2 | 1 | 17.4 | 1 | 17.9 | 1
EMPIRE BAY | 13.5 | 0.99 | 11.5 | 0.99 | 12.5 | 0.99 | 12.7 | 1 | 11.4 | 1 | 10.7 | 1
ENGADINE | 28.7 | 0.99 | 27.3 | 1 | 22.3 | 1 | 30.5 | 1 | 28.3 | 1 | 26 | 1
EPPING | 49.3 | 1 | 51.6 | 1 | 49.4 | 1 | 47 | 1 | 44.8 | 1 | 42.5 | 1
ERINA | 32.2 | 0.99 | 30 | 0.98 | 29.7 | 0.99 | 26.7 | 0.98 | 24.4 | 0.93 | 24.7 | 0.97
FLEMINGTON | 45.3 | 0.96 | 42.2 | 0.95 | 40 | 0.95 | 33.3 | 0.95 | 34.1 | 0.95 | 32.5 | 0.95
GALSTON | 10.5 | 0.96 | 9.5 | 0.97 | 9.7 | 0.97 | 9.8 | 0.99 | 9.4 | 0.99 | 8.9 | 0.99
GATESHEAD | 18.5 | 0.9 | 14.3 | 0.9 | 17.9 | 0.9 | 16.5 | 0.9 | 14.9 | 0.9 | 14.7 | 0.9
GORE HILL | 45.1 | 0.97 | 45.2 | 0.96 | 42.7 | 0.97 | 43.4 | 0.92 | 42.8 | 0.92 | 41.4 | 0.93
GREEN SQUARE | 54.4 | 0.99 | 60.6 | 0.99 | 54.8 | 0.99 | 45.3 | 1 | 44.6 | 1 | 40.4 | 1
GREENACRE |  |  |  |  | 53.6 | 0.9 |  |  | 5 | 0.9 | 39.6 | 0.9
GREENACRE PARK | 52.6 | 0.98 | 57 | 0.98 | 0 |  | 47 | 0.99 | 35.8 | 1 | 0
HARBORD | 18.4 | 0.91 | 15.9 | 0.92 | 18.1 | 0.92 | 23.8 | 0.96 | 22.4 | 0.96 | 23.8 | 0.96
HOMEBUSH BAY | 40.8 | 0.99 | 40.6 | 0.99 | 40.7 | 0.98 | 34.7 | 1 | 32.5 | 1 | 33.7 | 1
HORNSBY | 66.3 | 0.99 | 66.1 | 0.99 | 59.2 | 0.99 | 68.3 | 1 | 63.3 | 0.99 | 60.8 | 0.99
HUNTERS HILL | 57.4 | 0.92 | 56.6 | 0.99 | 63.2 | 1 | 55.4 | 0.95 | 49.7 | 0.99 | 50.1 | 0.98
HURSTVILLE NORTH | 22.6 | 0.98 | 23.6 | 0.99 | 22.9 | 0.99 | 20.1 | 1 | 19.5 | 1 | 18.2 | 1
JANNALI | 31.7 | 0.99 | 25.1 | 1 | 31.1 | 0.9 | 33.9 | 0.99 | 33.6 | 0.9 | 29.5 | 0.9
JESMOND | 45.4 | 0.98 | 34.6 | 0.99 | 42.8 | 0.99 | 37.5 | 1 | 34.3 | 1 | 32.2 | 1
JEWELLS | 17.2 | 0.98 | 12.6 | 0.99 | 15.8 | 0.99 | 13.7 | 1 | 12.1 | 1 | 11.7 | 1
KILLARNEY | 11.9 | 0.99 | 12.6 | 0.99 | 14.4 | 0.99 | 14.8 | 0.98 | 13.8 | 0.98 | 12.7 | 0.98
KINGSFORD | 52.2 | 0.99 | 53.1 | 0.99 | 54.9 | 1 | 58 | 1 | 58 | 1 | 57.4 | 1
KIRRAWEE | 39.6 | 0.9 | 36.4 | 0.92 | 37.9 | 0.99 | 41.9 | 0.89 | 39.6 | 1 | 37.7 | 0.99
KOGARAH | 74.4 | 0.99 | 66.1 | 0.99 | 65.7 | 0.99 | 62 | 1 | 59.9 | 1 | 57.2 | 1
KOTARA | 23.7 | 0.98 | 19.9 | 0.98 | 21.4 | 1 | 18 | 0.99 | 15.6 | 1 | 14.4 | 1
KURNELL SOUTH | 5.2 | 0.93 | 4.6 | 0.98 | 5.8 | 0.98 | 5.5 | 0.99 | 5.5 | 0.94 | 5.9 | 0.99
KURRI | 31.2 | 0.98 | 26.9 | 0.98 | 29.2 | 0.98 | 24.2 | 0.91 | 22.3 | 1 | 23.3 | 1
LAKE MUNMORAH | 24.7 | 0.99 | 19.2 | 0.99 | 23.2 | 0.99 | 20.4 | 1 | 19.2 | 1 | 18.7 | 1
LEICHHARDT | 37.4 | 0.98 | 36.7 | 0.99 | 36.3 | 1 | 45.6 | 0.99 | 40.2 | 1 | 37.9 | 1
LEIGHTONFIELD | 22.4 | 0.94 | 21.7 | 0.95 | 20.2 | 0.95 | 19.6 | 0.97 | 18.5 | 0.97 | 18.7 | 0.97
LIDCOMBE | 17.5 | 0.91 | 18.7 | 0.9 | 17.8 | 0.91 | 14.7 | 0.92 | 15.6 | 0.96 | 14.1 | 0.94
LINDFIELD | 33.6 | 0.98 | 28.5 | 0.87 | 29.7 | 0.88 | 36.5 | 0.87 | 29.1 | 0.84 | 31.1 | 0.85
LISAROW | 23.1 | 0.98 | 22.3 | 0.98 | 22.4 | 0.99 | 20.9 | 0.99 | 19.6 | 0.99 | 18.9 | 1
LONG JETTY | 45.4 | 0.9 | 36.2 | 0.9 | 42.9 | 0.9 | 44.1 | 0.9 | 41.4 | 0.9 | 39.3 | 0.9
MACQUARIE PARK | 82 | 0.98 | 88.5 | 0.99 | 65.2 | 0.99 | 72.8 | 1 | 54.8 | 0.99 | 50.6 | 1
MAITLAND | 25.1 | 0.97 | 23.4 | 0.98 | 23.6 | 0.98 | 17.1 | 0.99 | 16.2 | 1 | 16 | 1
MANLY | 16.2 | 0.91 | 13.7 | 0.91 | 15.5 | 0.91 | 19.2 | 0.95 | 20.7 | 0.95 | 17.1 | 0.95
MAROUBRA | 43.7 | 0.98 | 42.5 | 0.9 | 42.4 | 0.9 | 47.3 | 0.9 | 44.5 | 0.9 | 42.8 | 0.9
MARRICKVILLE | 44.6 | 0.98 | 49.5 | 0.99 | 44.9 | 0.99 | 50.8 | 1 | 49.3 | 1 | 46.9 | 1
MARYLAND | 26.5 | 0.98 | 21.9 | 0.99 | 25.4 | 0.99 | 18 | 1 | 14.9 | 1 | 14.3 | 1
MASCOT | 31.8 | 0.93 | 30.9 | 0.87 | 33.2 | 0.97 | 25.4 | 0.95 | 28.5 | 1 | 24.3 | 0.99
MAYFIELD WEST | 19.6 | 0.97 | 22.4 | 0.96 | 21.5 | 0.97 | 20.2 | 0.97 | 19.3 | 0.97 | 19.8 | 0.98
MEADOWBANK | 72.7 | 0.93 | 65.1 | 0.93 | 66.1 | 0.95 | 59.4 | 0.98 | 54.8 | 0.98 | 54.2 | 0.98
MEDOWIE | 14.7 | 0.99 | 11.9 | 0.99 | 15.1 | 0.99 | 10.9 | 1 | 10.5 | 1 | 10.9 | 1
MENAI | 43.5 | 0.99 | 39.7 | 0.99 | 41.7 | 0.99 | 41.2 | 0.99 | 36.5 | 0.99 | 34.4 | 0.99
MERRIWA | 3.2 | 0.99 | 2.4 | 0.99 | 3.2 | 0.99 | 3 | 1 | 2.9 | 1 | 2.8 | 1
METFORD | 39.6 | 0.99 | 39 | 0.99 | 41.7 | 0.99 | 30.7 | 1 | 30.6 | 1 | 29.1 | 1
MILPERRA | 42 | 0.97 | 43.8 | 0.96 | 43.3 | 0.98 | 41.5 | 0.97 | 41.3 | 0.97 | 36 | 0.99
MIRANDA | 32 | 0.94 | 30.6 | 0.96 | 32.3 | 0.96 | 30.3 | 0.98 | 28.3 | 0.98 | 27.3 | 0.97
MITCHELL LINE | 6.3 | 1 | 6.6 | 1 | 7.6 | 1 | 6.8 | 1 | 7.5 | 1 | 7.2 | 1
MITCHELLS FLAT | 1.8 | 1 | 1.4 | 1 | 1.6 | 1 | 1.2 | 1 | 1.1 | 1 | 1.1 | 0.99
MONA VALE | 34.9 | 0.93 | 31.5 | 0.9 | 34.8 | 0.9 | 34.8 | 0.96 | 32.9 | 0.9 | 30.5 | 0.9
MOONAN | 0.7 | 0.9 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 0.9
MORISSET | 27.9 | 0.98 | 22.9 | 0.99 | 26.3 | 0.99 | 22.5 | 1 | 20.9 | 1 | 20.7 | 1
MORTDALE | 45.7 | 0.99 | 40.6 | 0.99 | 43.8 | 0.99 | 44.6 | 1 | 41.8 | 1 | 38.9 | 1
MOSMAN | 67.4 | 0.99 | 56.7 | 1 | 66.3 | 1 | 80 | 1 | 75.1 | 1 | 69 | 1
MOUNT HUTTON | 16.9 | 0.99 | 15.1 | 1 | 18.2 | 1 | 15 | 1 | 14 | 1 | 12.6 | 1
MUSWELLBROOK | 19.8 | 0.9 | 14 | 0.9 | 15.5 | 0.9 | 13.9 | 0.9 | 13.2 | 0.9 | 13.1 | 0.9
NARRABEEN | 13.6 | 0.94 | 11.3 | 0.94 | 13 | 0.94 | 14.2 | 0.96 | 13 | 0.96 | 12.3 | 0.9
NELSON BAY | 27 | 0.99 | 21.9 | 0.99 | 22.7 | 1 | 23.5 | 1 | 22.9 | 1 | 20.8 | 1
NEW LAMBTON | 17.5 | 0.95 | 15.6 | 0.96 | 16.7 | 0.96 | 12.7 | 0.97 | 11.9 | 0.97 | 11.6 | 0.97
NEWCASTLE CBD | 37.4 | 0.99 | 35.8 | 0.98 | 43.4 | 0.99 | 33.2 | 1 | 34.6 | 1 | 29.4 | 1
NEWPORT | 14.8 | 0.99 | 11.6 | 0.99 | 13.9 | 0.99 | 18.9 | 0.98 | 15.6 | 0.98 | 18.3 | 0.98
NORAVILLE | 26.8 | 0.94 | 20.5 | 0.94 | 24.9 | 0.94 | 24.4 | 0.98 | 24.1 | 0.98 | 22.3 | 0.98
NORTH HEAD | 14.6 | 0.92 | 17 | 0.92 | 17.2 | 0.92 | 17.8 | 0.93 | 15.1 | 0.93 | 12.2 | 0.93
NORTH SYDNEY | 55.1 | 0.99 | 58.4 | 0.99 | 57.1 | 0.9 | 50.8 | 0.98 | 50.7 | 1 | 48.6 | 0.9
NULKABA | 16.5 | 0.98 | 15.8 | 0.97 | 16.1 | 0.98 | 12.2 | 0.99 | 13 | 1 | 12.7 | 0.99
OLYMPIC PARK | 31.3 | 1 | 30.3 | 0.99 | 30.5 | 0.9 | 25.4 | 1 | 23.6 | 0.9 | 23.3 | 0.9
PADDINGTON | 29.5 | 0.97 | 29.1 | 0.99 | 30 | 0.99 | 32 | 0.99 | 32 | 1 | 29.9 | 1
PAXTON | 7.3 | 0.9 | 6 | 0.9 | 6.5 | 0.9 | 5.9 | 0.9 | 5.4 | 0.9 | 5.3 | 0.9
PEATS RIDGE | 10.9 | 0.96 | 10.1 | 0.96 | 13 | 0.7 | 9.6 | 0.99 | 10.4 | 0.86 | 9.3 | 0.99
PELICAN | 12.5 | 0.99 | 9.8 | 0.99 | 10 | 1 | 11.1 | 1 | 10.1 | 0.99 | 9.3 | 1
PENNANT HILLS | 77.7 | 0.96 | 68 | 0.96 | 70.8 | 1 | 69.2 | 0.97 | 60.1 | 0.96 | 60 | 0.99
PORT BOTANY | 18.3 | 0.93 | 18.4 | 0.96 | 16 | 0.96 | 17.3 | 0.96 | 15.2 | 0.96 | 15.1 | 0.97
POTTS HILL | 43 | 0.99 | 39.9 | 0.99 | 39.1 | 0.83 | 37 | 1 | 34.2 | 1 | 32.9 | 0.9
PUNCHBOWL | 40 | 0.99 | 39.3 | 1 | 37.2 | 1 | 38.2 | 1 | 37.3 | 1 | 35.1 | 1
PYMBLE | 31.4 | 0.91 | 30.8 | 0.92 | 29 | 0.92 | 30.4 | 0.98 | 30.1 | 0.98 | 26.3 | 0.98
RATHMINES | 17 | 0.99 | 12.7 | 0.99 | 15.8 | 0.99 | 12.9 | 1 | 13.4 | 1 | 11 | 1
RAYMOND TERRACE | 20.9 | 0.99 | 20.7 | 0.99 | 23 | 0.99 | 21.1 | 1 | 19.4 | 1 | 18.6 | 1
REVESBY | 45.6 | 0.98 | 45 | 0.98 | 47.7 | 0.94 | 43.3 | 0.99 | 40.9 | 0.98 | 39.6 | 0.98
RIVERWOOD | 26.5 | 0.92 | 29.6 | 0.95 | 29.5 | 0.95 | 27 | 0.96 | 27.4 | 0.97 | 26.1 | 0.94
ROCKDALE | 35.6 | 1 | 39.4 | 1 | 41.3 | 1 | 39.8 | 1 | 38.1 | 1 | 38.5 | 1
ROSE BAY | 41.2 | 0.99 | 36.5 | 1 | 41.8 | 0.9 | 48.4 | 1 | 45.7 | 1 | 41.6 | 0.9
ROTHBURY | 12.2 | 0.79 | 11.4 | 1 | 12 | 0.9 | 7.3 | 0.99 | 8.3 | 0.9 | 8.2 | 0.9
ROUCHEL | 0.9 | 0.9 | 1.1 | 0.96 | 1.1 | 0.96 | 0.9 | 0.9 | 0.8 | 0.97 | 1.1 | 0.96
RUTHERFORD | 29 | 0.99 | 25.9 | 0.97 | 29.1 | 0.98 | 22.7 | 0.99 | 22.4 | 0.99 | 24 | 0.99
SANS SOUCI | 17.2 | 0.99 | 15.6 | 0.98 | 16.8 | 0.98 | 16.7 | 0.99 | 16.2 | 0.99 | 15.3 | 0.99
SCONE | 17.3 | 0.99 | 13.4 | 0.99 | 14 | 0.99 | 13.4 | 0.99 | 12.4 | 1 | 12.9 | 0.99
SEFTON | 45.3 | 0.96 | 49.4 | 0.95 | 48.5 | 0.96 | 42 | 0.97 | 40.9 | 0.97 | 39 | 0.97
SINGLETON | 18.4 | 0.9 | 16.6 | 0.9 | 16.8 | 0.9 | 15 | 0.9 | 14.2 | 0.9 | 14.8 | 0.9
SINGLETON NORTH | 17.6 | 0.96 | 15.1 | 0.94 | 15.9 | 0.99 | 12.4 | 0.96 | 11.6 | 0.95 | 11.5 | 1
SOMERSBY | 14.8 | 0.96 | 16.7 | 0.98 | 14.6 | 0.97 | 17.7 | 0.98 | 17.2 | 0.97 | 17.3 | 0.98
ST IVES | 45.8 | 0.97 | 40.3 | 0.97 | 42.3 | 0.96 | 46.4 | 0.97 | 43.3 | 0.97 | 40.8 | 0.97
ST PETERS | 58.2 | 0.99 | 65.8 | 0.99 | 64.9 | 0.99 | 56.6 | 1 | 55.4 | 1 | 53.9 | 1
STOCKTON | 9 | 0.99 | 6.4 | 1 | 8.8 | 0.99 | 7.1 | 1 | 6.5 | 1 | 6.2 | 1
STRATHFIELD SOUTH |  |  | 27.1 | 0.9 | 27.8 | 0.99 | 14 | 1 | 25.7 | 1 | 25.4 | 1
SUMMER HILL |  |  |  |  | 42.4 | 0.9 |  |  | 3.2 | 0.9 | 24.9 | 0.9
SURRY HILLS | 26.3 | 0.94 | 27.5 | 0.93 | 29.9 | 0.9 | 25.5 | 0.94 | 25.2 | 0.94 | 24.5 | 0.9
SWANSEA | 16.2 | 0.99 | 11.6 | 1 | 15.1 | 1 | 13.3 | 1 | 12.1 | 1 | 11.8 | 1
TANILBA BAY | 10.3 | 0.98 | 9.5 | 0.99 | 11.3 | 0.99 | 10.2 | 0.99 | 9.4 | 1 | 9.3 | 1
TARRO | 17.6 | 0.95 | 19.9 | 0.95 | 19.2 | 0.96 | 16.3 | 0.96 | 15.8 | 0.97 | 15.5 | 0.96
TELARAH | 14.9 | 0.99 | 12.5 | 1 | 13.2 | 1 | 9.9 | 1 | 9.3 | 1 | 8.9 | 1
TERREY HILLS | 14.3 | 0.94 | 15 | 0.94 | 14 | 0.94 | 13.9 | 0.97 | 12.4 | 0.97 | 12.2 | 0.97
THORNTON | 33.8 | 0.96 | 27.5 | 0.95 | 29.3 | 0.94 | 22.4 | 0.93 | 19.8 | 0.93 | 21.2 | 0.93
TIGHES HILL | 24.5 | 0.98 | 21.8 | 0.97 | 21.4 | 0.97 | 23.8 | 0.97 | 21 | 0.98 | 21.8 | 0.98
TOMAGO | 10.6 | 0.94 | 10.3 | 0.94 | 10.7 | 0.95 | 10.2 | 0.96 | 10.2 | 0.96 | 11.1 | 0.96
TOMALPIN | 1.3 | 1 | 1.5 | 0.92 | 1.7 | 0.92 | 1.3 | 0.99 | 1.9 | 0.95 | 1.9 | 0.93
TOMAREE | 17.7 | 0.99 | 13.9 | 0.99 | 13.3 | 1 | 18.6 | 1 | 13.9 | 1 | 13.7 | 1
TOP RYDE | 43.4 | 0.99 | 49.6 | 0.99 | 45.7 | 0.99 | 41.1 | 0.98 | 37 | 1 | 37.3 | 1
TORONTO WEST | 21 | 0.99 | 17 | 0.99 | 18.9 | 0.99 | 16.7 | 1 | 16 | 1 | 15.4 | 1
TURRAMURRA | 37.7 | 0.99 | 33.4 | 1 | 32.9 | 1 | 38.4 | 1 | 36.3 | 1 | 34.6 | 1
UMINA | 32.3 | 0.95 | 27.8 | 0.95 | 29.7 | 0.95 | 29.3 | 0.98 | 25.7 | 0.98 | 24.4 | 0.98
VALES POINT | 8.4 | 0.9 | 6.9 | 0.83 | 6 | 0.83 | 8 | 0.74 | 6.4 | 0.68 | 6.3 | 0.6
WAMBERAL | 16.2 | 0.99 | 13 | 1 | 14.8 | 1 | 16 | 1 | 14.8 | 1 | 13.9 | 1
WAVERLEY | 33.9 | 1 | 30.2 | 0.9 | 32.7 | 0.9 | 46 | 1 | 42.1 | 0.9 | 40.6 | 0.9
WEST GOSFORD | 43.3 | 0.99 | 46.5 | 0.98 | 46.4 | 0.99 | 40.6 | 1 | 39.1 | 1 | 36.8 | 1
WILLIAMTOWN | 5.1 | 0.99 | 5.7 | 1 | 2.9 | 0.99 | 5.7 | 1 | 4.1 | 1 | 3 | 1
WOY WOY | 21.3 | 0.95 | 18.4 | 0.96 | 19.6 | 0.96 | 19.2 | 0.97 | 16.9 | 0.97 | 21.5 | 0.97
WYONG | 40.4 | 0.99 | 37.4 | 0.99 | 42.2 | 0.99 | 35.2 | 1 | 31.7 | 1 | 32.8 | 1
ZETLAND | 58.7 | 0.97 | 59 | 0.98 | 66.2 | 1 | 55.8 | 0.95 | 52.2 | 1 | 49.1 | 1
MATRAVILLE | 33.6 | 0.9 | 31.8 | 0.92 | 34.6 | 0.92 | 38.9 | 0.96 | 37.9 | 0.96 | 36.3 | 0.96
RNS HOSPITAL | 11.8 | 0.99 | 11.9 | 0.99 | 13.5 | 0.99 | 9.5 | 0.99 | 15.7 | 0.99 | 8.5 | 1
LEMINGTON | 2.1 | 0.97 | 1.7 | 0.98 | 2.3 | 0.96 | 1.8 | 0.97 | 1.5 | 1 | 1.9 | 0.97
MOUNT THORLEY | 5.5 | 0.99 | 5.2 | 0.99 | 5.1 | 1 | 4.7 | 1 | 4.3 | 0.99 | 5.1 | 1
NEWDELL | 4 | 0.97 | 3.8 | 0.98 | 3.5 | 0.97 | 3.4 | 0.98 | 4 | 0.98 | 3.5 | 0.97
GWAWLEY BAY | 29.6 | 0.99 | 28.4 | 0.99 | 29.4 | 0.99 | 27.6 | 1 | 24.3 | 0.99 | 23.1 | 0.99
LUCAS HEIGHTS | 8.1 | 0.91 | 8.1 | 0.91 | 8.4 | 0.91 | 7.8 | 0.97 | 7.5 | 0.97 | 7.7 | 0.97

## Demand Forecast - (ZS)
Demand Forecast - Zone Substation
Name | Summer | [9 empty] | Winter
| 2023/24 (MVA) | 2023/24 (PF) | 2024/25 (MVA) | 2024/25 (PF) | 2025/26 (MVA) | 2025/26 (PF) | 2026/27 (MVA) | 2026/27 (PF) | 2027/28 (MVA) | 2027/28 (PF) | 2024 (MVA) | 2024 (PF) | 2025 (MVA) | 2025 (PF) | 2026 (MVA) | 2026 (PF) | 2027 (MVA) | 2027 (PF) | 2028 (MVA) | 2028 (PF)
ABERDEEN | 5.5 | 1 | 5.8 | 1 | 5.9 | 1 | 6.2 | 1 | 6.8 | 1 | 4 | 1 | 4.3 | 1 | 4.4 | 1 | 4.9 | 1 | 5.4 | 1
ADAMSTOWN | 27.4 | 1 | 27.2 | 1 | 26.7 | 1 | 26.7 | 1 | 26.9 | 1 | 23.1 | 1 | 23.2 | 1 | 22.9 | 1 | 22.9 | 1 | 23.3 | 1
ARGENTON | 35.9 | 0.99 | 35.6 | 0.99 | 35.4 | 0.99 | 35.4 | 0.99 | 35.8 | 0.99 | 26.9 | 0.99 | 26.8 | 0.99 | 26.7 | 0.99 | 27.1 | 0.99 | 28 | 0.99
AUBURN | 28.9 | 0.94 | 29 | 0.94 | 28.8 | 0.94 | 28.5 | 0.94 | 27.9 | 0.94 | 23 | 0.95 | 23.7 | 0.95 | 24.3 | 0.95 | 24.6 | 0.95 | 25.3 | 0.95
AVOCA | 33.8 | 1 | 33.4 | 1 | 33.1 | 1 | 33.3 | 1 | 33.6 | 1 | 31.2 | 1 | 30.7 | 1 | 30.3 | 1 | 30.5 | 1 | 31 | 1
AVONDALE | 12.4 | 1 | 13 | 1 | 14.8 | 1 | 15.3 | 1 | 15.9 | 1 | 8.9 | 1 | 12.2 | 1 | 12.7 | 1 | 13.3 | 1 | 14 | 1
BAERAMI | 0.7 | 0.95 | 0.7 | 0.95 | 0.7 | 0.95 | 0.7 | 0.95 | 0.7 | 0.95 | 0.5 | 0.97 | 0.5 | 0.97 | 0.5 | 0.97 | 0.5 | 0.97 | 0.5 | 0.97
BALGOWLAH NORTH | 29 | 1 | 29.7 | 1 | 30.1 | 1 | 30.6 | 1 | 31 | 1 | 31.5 | 1 | 31.3 | 1 | 31.1 | 1 | 31.3 | 1 | 31.7 | 1
BANKSTOWN | 45.8 | 0.99 | 46.3 | 0.99 | 45.2 | 0.99 | 45 | 0.99 | 45.6 | 0.99 | 40.3 | 1 | 41.7 | 1 | 42.1 | 1 | 42.9 | 1 | 43.7 | 1
BASS HILL | 20.5 | 1 | 20.2 | 1 | 20 | 1 | 19.9 | 1 | 19.9 | 1 | 15.9 | 1 | 16.2 | 1 | 16.4 | 1 | 16.6 | 1 | 16.8 | 1
BEACON HILL | 18.5 | 1 | 18.7 | 1 | 18.4 | 1 | 18.2 | 1 | 18.1 | 1 | 19.3 | 0.99 | 19.9 | 0.99 | 20.4 | 0.99 | 21 | 0.99 | 21.3 | 1
BELMORE PARK | 34.4 | 0.98 | 77.3 | 0.95 | 76.4 | 0.95 | 76 | 0.95 | 75.3 | 0.95 | 16.4 | 0.9 | 54.4 | 0.92 | 55 | 0.92 | 55.3 | 0.92 | 56.1 | 0.92
BELROSE | 29.1 | 0.97 | 29.7 | 0.97 | 29.7 | 0.97 | 29.8 | 0.97 | 29.9 | 0.97 | 26.1 | 0.96 | 26 | 0.96 | 25.6 | 0.96 | 25.7 | 0.96 | 25.9 | 0.96
BERKELEY VALE | 43.1 | 0.98 | 45.8 | 0.98 | 46 | 0.98 | 46.3 | 0.98 | 46.7 | 0.98 | 39.7 | 0.99 | 40.1 | 0.99 | 40.4 | 0.99 | 40.9 | 0.99 | 41.6 | 0.99
BEROWRA | 21.8 | 0.93 | 20.9 | 0.93 | 20.4 | 0.93 | 20.5 | 0.93 | 20.8 | 0.93 | 22.2 | 0.97 | 21.9 | 0.97 | 21.9 | 0.97 | 22.2 | 0.97 | 22.6 | 0.97
BLACKWATTLE BAY | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
BLAKEHURST | 24.5 | 0.98 | 25.8 | 0.98 | 26.5 | 0.98 | 27.3 | 0.98 | 28 | 0.98 | 24.4 | 0.95 | 25.1 | 0.95 | 25.4 | 0.95 | 25.9 | 0.95 | 26.4 | 0.95
BOTANY | 27.9 | 0.99 | 28 | 0.99 | 27.7 | 0.99 | 27.5 | 0.99 | 27.6 | 0.99 | 24.8 | 1 | 25.1 | 1 | 25.3 | 1 | 25.6 | 1 | 26.1 | 1
BRANDY HILL | 11.5 | 1 | 11.3 | 1 | 11.3 | 1 | 11.5 | 1 | 11.7 | 1 | 7.3 | 1 | 7.4 | 1 | 7.6 | 1 | 7.9 | 1 | 8.2 | 1
BRANXTON | 15.3 | 0.99 | 15.4 | 0.99 | 15.6 | 0.99 | 16 | 0.99 | 16.7 | 0.99 | 11.9 | 1 | 12.3 | 1 | 12.8 | 1 | 13.5 | 1 | 14.2 | 1
BROADMEADOW | 23.3 | 0.99 | 22.6 | 0.99 | 22.2 | 0.99 | 22 | 0.99 | 22.3 | 0.99 | 20.9 | 0.99 | 21 | 0.99 | 21.1 | 0.99 | 21.6 | 0.99 | 22.2 | 0.99
BROOKVALE | 36.3 | 1 | 36 | 1 | 35 | 1 | 34 | 1 | 33.3 | 1 | 34 | 1 | 33.8 | 1 | 33.7 | 1 | 34.3 | 1 | 35.3 | 1
BURWOOD | 73.4 | 0.99 | 75 | 0.99 | 76.4 | 0.99 | 76.7 | 0.99 | 77.4 | 0.99 | 58.3 | 1 | 61.8 | 1 | 63.6 | 1 | 65.2 | 1 | 66.4 | 1
CAMPBELL ST | 43 | 0.97 | 23.7 | 0.97 | 23.9 | 0.97 | 21.4 | 0.97 | 19.9 | 0.97 | 40.1 | 0.99 | 22.1 | 0.99 | 22.9 | 0.99 | 24 | 0.99 | 25.7 | 0.99
CAMPERDOWN | 30.8 | 1 | 35.4 | 0.99 | 35.6 | 0.99 | 36.8 | 0.99 | 36.6 | 0.99 | 22.3 | 1 | 27.2 | 1 | 29.9 | 1 | 30.5 | 1 | 31.1 | 1
CAMPERDOWN | 2.8 | 0.92 | 0 |  | 0 |  | 0 |  | 0 |  | 2.5 | 0.95 | 0 |  | 0 |  | 0 |  | 0
CAMPSIE | 72.7 | 0.99 | 73.6 | 0.99 | 74 | 0.99 | 74.7 | 0.99 | 75.3 | 0.99 | 67.1 | 0.99 | 68.2 | 0.99 | 68.9 | 0.99 | 70.1 | 0.99 | 71.2 | 0.99
CARDIFF | 20.2 | 0.99 | 19.8 | 0.99 | 19.5 | 0.99 | 19.4 | 0.99 | 19.5 | 0.99 | 14.6 | 1 | 14.5 | 1 | 14.5 | 1 | 14.6 | 1 | 15 | 1
CAREEL BAY | 11.3 | 0.99 | 11.2 | 0.99 | 11.3 | 0.99 | 11.4 | 0.99 | 11.6 | 0.99 | 12.2 | 0.99 | 12 | 0.99 | 11.8 | 0.99 | 11.9 | 0.99 | 12 | 0.99
CARINGBAH | 23.8 | 0.93 | 25.6 | 0.93 | 25.5 | 0.93 | 25.4 | 0.93 | 25.2 | 0.93 | 23.2 | 0.92 | 23.9 | 0.92 | 24.5 | 0.92 | 25.1 | 0.92 | 25.8 | 0.92
CASTLE COVE | 56.7 | 0.98 | 55.4 | 0.98 | 54.3 | 0.98 | 53.9 | 0.98 | 53.6 | 0.98 | 40.6 | 0.82 | 40.6 | 0.82 | 40.8 | 0.82 | 41.4 | 0.81 | 42.3 | 0.81
CESSNOCK SOUTH | 31 | 0.99 | 32.3 | 0.99 | 32.8 | 0.99 | 33.4 | 0.99 | 33.8 | 0.99 | 19.6 | 1 | 21.1 | 1 | 21.8 | 1 | 22.7 | 1 | 23.3 | 1
CHARLESTOWN | 32.1 | 1 | 31.1 | 1 | 30.5 | 0.99 | 30.2 | 0.99 | 30 | 0.99 | 27.9 | 1 | 28.2 | 1 | 28.1 | 1 | 28.3 | 1 | 28.5 | 1
CHARMHAVEN | 45.7 | 1 | 44.6 | 1 | 43.8 | 1 | 43.7 | 1 | 44.2 | 1 | 35 | 1 | 35.2 | 1 | 35.2 | 1 | 35.7 | 1 | 36.3 | 1
CHATSWOOD | 45.4 | 0.92 | 46.7 | 0.92 | 46.8 | 0.92 | 47.1 | 0.92 | 47.9 | 0.92 | 40.6 | 0.95 | 42.1 | 0.95 | 42.3 | 0.95 | 42.8 | 0.95 | 43.7 | 0.95
CITY CENTRAL | 79.8 | 1 | 83.8 | 1 | 85.2 | 1 | 84.8 | 1 | 83.4 | 1 | 66.9 | 1 | 71.6 | 1 | 74.5 | 1 | 77 | 1 | 79 | 1
CITY EAST | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
CITY NORTH | 90.8 | 1 | 93.5 | 1 | 91.5 | 1 | 89.4 | 1 | 87.5 | 1 | 56 | 0.97 | 55.8 | 0.97 | 56.2 | 0.97 | 58.1 | 0.96 | 60.3 | 0.96
CITY SOUTH | 93.6 | 1 | 97.8 | 1 | 98.1 | 1 | 97.1 | 1 | 95.9 | 1 | 77.1 | 1 | 81.1 | 1 | 82.7 | 1 | 83.8 | 1 | 85.8 | 1
CLOVELLY | 36.9 | 1 | 38.9 | 1 | 39.7 | 1 | 40.4 | 1 | 41.1 | 1 | 41.2 | 1 | 41.8 | 1 | 41.6 | 1 | 42 | 1 | 42.6 | 1
CONCORD | 45.7 | 0.96 | 46.8 | 0.96 | 46.7 | 0.96 | 46.6 | 0.96 | 46.6 | 0.96 | 31.3 | 0.98 | 33 | 0.98 | 33.5 | 0.98 | 34.3 | 0.98 | 34.8 | 0.98
CRONULLA | 54.3 | 0.98 | 57.5 | 0.98 | 59.4 | 0.98 | 60.8 | 0.98 | 61.4 | 0.98 | 58.2 | 0.99 | 60.1 | 0.99 | 61 | 0.99 | 62.1 | 0.99 | 62.9 | 0.99
CROUDACE BAY | 21.5 | 1 | 21.1 | 1 | 20.7 | 1 | 20.8 | 1 | 21 | 1 | 15.6 | 1 | 15.6 | 1 | 15.7 | 1 | 15.9 | 1 | 16.2 | 1
CROWS NEST | 34.4 | 0.9 | 38.9 | 0.9 | 39.2 | 0.9 | 39.3 | 0.9 | 39.8 | 0.9 | 37.9 | 0.9 | 43.3 | 0.9 | 44.3 | 0.9 | 45.5 | 0.9 | 46.1 | 0.9
CROYDON | 33.1 | 0.99 | 32.8 | 0.99 | 32.5 | 0.99 | 32.8 | 0.99 | 33.4 | 0.99 | 37.3 | 0.99 | 37.3 | 0.99 | 37.3 | 0.99 | 37.6 | 0.99 | 38 | 0.99
DALLEY ST | 34.6 | 1 | 0 |  | 0 |  | 0 |  | 0 |  | 29.6 | 1 | 0 |  | 0 |  | 0 |  | 0
DARLING HARBOUR | 53.7 | 0.98 | 55.9 | 0.98 | 55.5 | 0.98 | 54.8 | 0.98 | 54.5 | 0.98 | 47.8 | 1 | 48.2 | 1 | 48.5 | 1 | 49.8 | 1 | 51.6 | 1
DARLINGHURST | 28.1 | 0.98 | 27.3 | 0.98 | 26.6 | 0.98 | 26.1 | 0.98 | 26.1 | 0.98 | 22.4 | 1 | 22 | 1 | 21.9 | 1 | 22.1 | 1 | 22.6 | 1
DEE WHY WEST | 35.7 | 0.93 | 36.5 | 0.93 | 37.2 | 0.93 | 38 | 0.93 | 38.6 | 0.93 | 41.4 | 0.98 | 42 | 0.98 | 42.3 | 0.98 | 43 | 0.98 | 43.6 | 0.98
DENMAN | 9.4 | 0.99 | 9.5 | 0.99 | 9.5 | 0.99 | 9.6 | 0.99 | 9.5 | 0.99 | 6.5 | 1 | 6.5 | 1 | 6.4 | 1 | 6.3 | 1 | 6.3 | 1
DOUBLE BAY | 53 | 0.93 | 53.3 | 0.93 | 52.3 | 0.93 | 51.5 | 0.93 | 51.1 | 0.93 | 54.4 | 1 | 54.4 | 1 | 53.6 | 1 | 53.6 | 1 | 54.1 | 1
DRUMMOYNE | 55.1 | 0.97 | 55.7 | 0.97 | 56.2 | 0.97 | 56.7 | 0.97 | 57.6 | 0.97 | 55.8 | 0.98 | 56 | 0.98 | 56 | 0.98 | 56.6 | 0.98 | 57.3 | 0.98
DULWICH HILL | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
EDGEWORTH | 29.1 | 0.99 | 29.7 | 0.99 | 29.8 | 0.99 | 29.9 | 0.99 | 30 | 0.99 | 18.9 | 1 | 19.7 | 1 | 20 | 1 | 20.3 | 1 | 20.5 | 1
EMPIRE BAY | 12.9 | 0.99 | 13 | 0.99 | 13.1 | 0.99 | 13.2 | 0.99 | 13.3 | 0.99 | 10.7 | 1 | 10.5 | 1 | 10.3 | 1 | 10.3 | 1 | 10.4 | 1
ENGADINE | 28.6 | 1 | 27.9 | 1 | 27.6 | 1 | 27.9 | 1 | 28.3 | 1 | 28.7 | 1 | 28.4 | 1 | 28.4 | 1 | 28.9 | 1 | 29.4 | 1
EPPING | 59 | 1 | 62.7 | 1 | 63.9 | 1 | 64.3 | 1 | 64.5 | 1 | 47.2 | 1 | 50.8 | 1 | 52.9 | 1 | 54.3 | 1 | 55.5 | 1
ERINA | 39.2 | 1 | 39.3 | 1 | 39.1 | 1 | 38.8 | 1 | 38.4 | 1 | 29.4 | 1 | 30.1 | 1 | 30.5 | 1 | 31.1 | 1 | 31.9 | 1
FLEMINGTON | 42.4 | 0.95 | 43.3 | 0.95 | 43.7 | 0.95 | 43.4 | 0.95 | 42.7 | 0.95 | 33.8 | 0.95 | 34.7 | 0.95 | 34.9 | 0.95 | 35.3 | 0.95 | 36 | 0.95
GALSTON | 10.6 | 0.97 | 10.7 | 0.97 | 11 | 0.97 | 11.1 | 0.97 | 11.3 | 0.97 | 9.2 | 0.99 | 9.6 | 0.99 | 9.8 | 0.99 | 10.1 | 0.99 | 10.3 | 0.99
GATESHEAD | 15.8 | 0.9 | 15.4 | 0.9 | 15 | 0.9 | 14.9 | 0.9 | 15.1 | 0.9 | 15.7 | 0.9 | 15.8 | 0.9 | 15.9 | 0.9 | 16.1 | 0.9 | 16.3 | 0.9
GORE HILL | 36 | 0.97 | 35 | 0.97 | 33.6 | 0.97 | 32.3 | 0.97 | 30.9 | 0.97 | 41.5 | 0.93 | 40.9 | 0.93 | 40.5 | 0.93 | 40.5 | 0.93 | 41.3 | 0.93
GREEN SQUARE | 55.5 | 0.99 | 66.2 | 0.99 | 66.1 | 0.99 | 65.3 | 0.99 | 63.7 | 0.99 | 48.2 | 1 | 51.4 | 1 | 57.6 | 1 | 58.8 | 1 | 59.8 | 1
GREENACRE | 59.7 | 0.9 | 57.6 | 0.9 | 55.9 | 0.9 | 54.8 | 0.9 | 54.2 | 0.9 | 37 | 0.9 | 36.6 | 0.9 | 36.5 | 0.9 | 36.9 | 0.9 | 37.5 | 0.9
GREENACRE PARK | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
HARBORD | 17.4 | 0.92 | 17.7 | 0.92 | 17.8 | 0.92 | 18.2 | 0.92 | 18.7 | 0.92 | 23.2 | 0.96 | 23.2 | 0.96 | 23.1 | 0.96 | 23.3 | 0.96 | 23.6 | 0.96
HOMEBUSH BAY | 41.2 | 0.98 | 42.4 | 0.98 | 39.5 | 0.98 | 38.9 | 0.98 | 38.3 | 0.98 | 31.6 | 1 | 33.2 | 1 | 31.4 | 1 | 32.6 | 1 | 33.7 | 1
HORNSBY | 70.3 | 0.99 | 71 | 0.99 | 70.6 | 0.99 | 70.7 | 0.99 | 71.1 | 0.99 | 62.2 | 0.99 | 62.2 | 0.99 | 61.8 | 0.99 | 62.2 | 0.99 | 63.1 | 0.99
HUNTERS HILL | 59.5 | 1 | 58.9 | 1 | 58.6 | 1 | 59.1 | 1 | 60 | 1 | 51.6 | 0.98 | 51.8 | 0.98 | 51.9 | 0.98 | 52.9 | 0.98 | 54.1 | 0.98
HURSTVILLE NORTH | 22.7 | 1 | 22.2 | 0.99 | 21.7 | 0.99 | 21.8 | 0.99 | 22 | 0.99 | 19.1 | 1 | 18.9 | 1 | 18.9 | 1 | 19.1 | 1 | 19.5 | 1
JANNALI | 30.5 | 0.9 | 30.1 | 0.9 | 29.8 | 0.9 | 29.9 | 0.9 | 30.1 | 0.9 | 32.8 | 0.9 | 33.2 | 0.9 | 33.3 | 0.9 | 33.6 | 0.9 | 33.9 | 0.9
JESMOND | 44.8 | 0.99 | 44 | 0.99 | 43.5 | 0.99 | 43.3 | 0.99 | 43.3 | 0.99 | 34.6 | 1 | 34.5 | 1 | 34.4 | 1 | 34.6 | 1 | 34.9 | 1
JEWELLS | 13.9 | 0.99 | 13.5 | 0.99 | 13.3 | 0.99 | 13.3 | 0.99 | 13.5 | 0.99 | 12.4 | 1 | 12.5 | 1 | 12.6 | 1 | 12.8 | 1 | 13 | 1
KILLARNEY | 13.2 | 0.99 | 13.1 | 0.99 | 13 | 0.99 | 13.2 | 0.99 | 13.5 | 0.99 | 13.6 | 0.98 | 13.4 | 0.98 | 13.4 | 0.98 | 13.6 | 0.98 | 14 | 0.98
KINGSFORD | 51.7 | 1 | 54.9 | 1 | 55 | 1 | 55.4 | 1 | 55.5 | 1 | 58 | 1 | 60 | 1 | 60.1 | 1 | 60.6 | 1 | 60.8 | 1
KIRRAWEE | 37.5 | 0.99 | 37.7 | 0.99 | 37.6 | 0.99 | 37.8 | 0.99 | 38.1 | 0.99 | 40.6 | 0.99 | 41.1 | 0.99 | 41.3 | 0.99 | 41.8 | 0.99 | 42.3 | 0.99
KOGARAH | 64 | 0.99 | 66.6 | 0.99 | 67.1 | 0.99 | 67.6 | 0.99 | 68.7 | 0.99 | 66.6 | 1 | 68.2 | 1 | 69.3 | 1 | 70.7 | 1 | 71.9 | 1
KOTARA | 21.5 | 1 | 20.7 | 1 | 20.3 | 1 | 20 | 1 | 20 | 1 | 15.8 | 1 | 15.9 | 1 | 16 | 1 | 16.3 | 1 | 16.6 | 1
KURNELL SOUTH | 5.4 | 0.98 | 6.2 | 0.98 | 6.8 | 0.98 | 7.1 | 0.98 | 7.1 | 0.98 | 5.8 | 0.99 | 6.5 | 0.99 | 6.9 | 0.99 | 7.2 | 0.99 | 7.2 | 0.99
KURRI | 30.9 | 0.98 | 30.6 | 0.98 | 30.6 | 0.98 | 30.6 | 0.98 | 30.9 | 0.98 | 24.2 | 1 | 25.3 | 1 | 25.6 | 1 | 26.1 | 1 | 26.7 | 1
LAKE MUNMORAH | 24.2 | 0.99 | 24.5 | 0.99 | 24.6 | 0.99 | 24.9 | 0.99 | 25.2 | 0.99 | 19.8 | 1 | 20 | 1 | 20.2 | 1 | 20.6 | 1 | 20.9 | 1
LEICHHARDT | 37.2 | 1 | 40.2 | 1 | 40.5 | 1 | 41.2 | 1 | 41.5 | 1 | 42.1 | 1 | 45 | 1 | 45.5 | 1 | 45.3 | 1 | 45.5 | 1
LEIGHTONFIELD | 23.4 | 0.95 | 25 | 0.95 | 25.2 | 0.95 | 25.5 | 0.95 | 25.8 | 0.95 | 20.9 | 0.97 | 22.4 | 0.97 | 22.7 | 0.97 | 23.1 | 0.97 | 23.6 | 0.97
LIDCOMBE | 19.7 | 0.91 | 21.9 | 0.91 | 23.4 | 0.91 | 24 | 0.91 | 24.1 | 0.91 | 14.2 | 0.94 | 17.2 | 0.94 | 19 | 0.94 | 20 | 0.94 | 20.2 | 0.94
LINDFIELD | 33 | 0.88 | 32.9 | 0.88 | 32.7 | 0.88 | 32.8 | 0.88 | 33.1 | 0.88 | 31.9 | 0.85 | 31.7 | 0.85 | 31.6 | 0.85 | 31.9 | 0.85 | 32.3 | 0.85
LISAROW | 23 | 1 | 23 | 1 | 23.9 | 1 | 24.1 | 1 | 24.2 | 1 | 19.5 | 1 | 19.4 | 1 | 20.1 | 1 | 20.4 | 1 | 20.7 | 1
LONG JETTY | 45.5 | 0.9 | 46.9 | 0.9 | 47.5 | 0.9 | 48.2 | 0.9 | 48.5 | 0.9 | 40.5 | 0.9 | 41.1 | 0.9 | 41 | 0.9 | 41.4 | 0.9 | 42 | 0.9
MACQUARIE PARK | 66.2 | 0.99 | 64.4 | 0.99 | 62.6 | 0.99 | 60.7 | 0.99 | 59.2 | 0.99 | 50 | 1 | 49.6 | 1 | 49 | 1 | 49.1 | 1 | 49.9 | 1
MAITLAND | 27.6 | 0.98 | 25.1 | 0.98 | 25.8 | 0.98 | 26.2 | 0.98 | 26.8 | 0.98 | 16.9 | 1 | 17 | 1 | 17.3 | 1 | 17.9 | 1 | 18.7 | 1
MANLY | 14.6 | 0.91 | 14.6 | 0.91 | 14.8 | 0.91 | 15.2 | 0.91 | 15.7 | 0.91 | 18.7 | 0.95 | 18.8 | 0.95 | 19 | 0.95 | 19.3 | 0.95 | 19.7 | 0.95
MAROUBRA | 43.6 | 0.9 | 44.9 | 0.9 | 45.7 | 0.9 | 46.4 | 0.9 | 46.8 | 0.9 | 47.4 | 0.9 | 48.5 | 0.9 | 49.1 | 0.9 | 49.7 | 0.9 | 50 | 0.9
MARRICKVILLE | 43.4 | 0.99 | 44.8 | 0.99 | 43.8 | 0.99 | 44.4 | 0.99 | 45.1 | 0.99 | 50.2 | 1 | 49.9 | 1 | 50.9 | 1 | 51.8 | 1 | 52.4 | 1
MARYLAND | 28.3 | 0.99 | 27.9 | 0.99 | 27.6 | 0.99 | 27.6 | 0.99 | 27.7 | 0.99 | 15.1 | 1 | 14.9 | 1 | 14.7 | 1 | 14.8 | 1 | 15.1 | 1
MASCOT | 33.8 | 0.97 | 35.3 | 0.97 | 35.5 | 0.97 | 35.3 | 0.97 | 34.8 | 0.97 | 26.4 | 0.99 | 27.7 | 0.99 | 29.1 | 0.99 | 30 | 0.99 | 30.7 | 0.99
MAYFIELD WEST | 23.7 | 0.97 | 23.7 | 0.97 | 23.9 | 0.97 | 23.9 | 0.97 | 24.1 | 0.97 | 21.7 | 0.98 | 22.6 | 0.98 | 22.9 | 0.98 | 23.3 | 0.98 | 23.9 | 0.98
MEADOWBANK | 74 | 0.95 | 76.1 | 0.95 | 76.9 | 0.95 | 78.1 | 0.95 | 79.3 | 0.95 | 54.7 | 0.98 | 55.5 | 0.98 | 55.4 | 0.98 | 56.6 | 0.98 | 58.4 | 0.98
MEDOWIE | 15.6 | 0.99 | 16 | 0.99 | 16.4 | 0.99 | 16.8 | 0.99 | 17.3 | 0.99 | 12 | 1 | 12.4 | 1 | 12.9 | 1 | 13.5 | 1 | 14 | 1
MENAI | 45 | 0.99 | 44.5 | 0.99 | 44.3 | 0.99 | 44.5 | 0.99 | 44.8 | 0.99 | 36.2 | 0.99 | 35.9 | 0.99 | 35.8 | 0.99 | 36.2 | 0.99 | 36.7 | 0.99
MERRIWA | 4.1 | 0.99 | 4.7 | 0.99 | 5.1 | 0.99 | 5.5 | 0.99 | 5.8 | 0.99 | 3.1 | 1 | 3.7 | 1 | 4.1 | 1 | 4.5 | 1 | 4.7 | 1
METFORD | 41.9 | 0.99 | 41.7 | 0.99 | 40.8 | 0.99 | 41.5 | 0.99 | 42.4 | 0.99 | 31.9 | 1 | 32.3 | 1 | 33.5 | 1 | 34.7 | 1 | 35.7 | 1
MILPERRA | 41.8 | 0.98 | 43.4 | 0.98 | 43.8 | 0.98 | 44.4 | 0.98 | 44.5 | 0.98 | 42.5 | 0.99 | 45.7 | 0.99 | 47.7 | 0.99 | 49.3 | 0.99 | 50.3 | 0.99
MIRANDA | 31.8 | 0.96 | 31.5 | 0.96 | 31.2 | 0.96 | 31 | 0.96 | 30.9 | 0.96 | 28.8 | 0.97 | 29 | 0.97 | 29.1 | 0.97 | 29.4 | 0.97 | 29.6 | 0.97
MITCHELL LINE | 8.2 | 1 | 8.4 | 1 | 8.4 | 1 | 8.4 | 1 | 8.4 | 1 | 7.4 | 1 | 7.9 | 1 | 8.1 | 1 | 8.2 | 1 | 8.3 | 1
MITCHELLS FLAT | 1.9 | 1 | 2 | 1 | 2 | 1 | 2.1 | 1 | 2.1 | 1 | 1.2 | 0.99 | 1.3 | 0.99 | 1.3 | 0.99 | 1.3 | 0.99 | 1.4 | 0.99
MONA VALE | 33.3 | 0.9 | 33.6 | 0.9 | 33.3 | 0.9 | 33.3 | 0.9 | 33.5 | 0.9 | 32 | 0.9 | 32 | 0.9 | 31.9 | 0.9 | 32.1 | 0.9 | 32.4 | 0.9
MOONAN | 0.8 | 0.9 | 0.8 | 0.9 | 0.8 | 0.9 | 0.8 | 0.9 | 0.8 | 0.9 | 1 | 0.9 | 1 | 0.9 | 1 | 0.9 | 1 | 0.9 | 1.1 | 0.9
MORISSET | 28.6 | 0.99 | 29.7 | 0.99 | 30.6 | 0.99 | 31.5 | 0.99 | 32.2 | 0.99 | 24 | 1 | 25.6 | 1 | 27.1 | 1 | 28.4 | 1 | 29.4 | 1
MORTDALE | 43.8 | 0.99 | 43.6 | 0.99 | 43.1 | 0.99 | 43.1 | 0.99 | 43.5 | 0.99 | 42 | 1 | 42 | 1 | 42 | 1 | 42.6 | 1 | 43.3 | 1
MOSMAN | 63 | 1 | 63 | 1 | 63.7 | 1 | 64.7 | 1 | 65.9 | 1 | 71.4 | 1 | 69.9 | 1 | 69 | 1 | 69.4 | 1 | 70.5 | 1
MOUNT HUTTON | 17.6 | 1 | 16.9 | 1 | 16.4 | 1 | 16.2 | 1 | 16.2 | 1 | 14.1 | 1 | 14.1 | 1 | 14 | 1 | 14.1 | 1 | 14.2 | 1
MUSWELLBROOK | 18.3 | 0.99 | 19.2 | 0.99 | 19.6 | 0.99 | 19.8 | 0.98 | 19.9 | 0.98 | 13.6 | 0.9 | 12.9 | 1 | 13.2 | 1 | 13.4 | 1 | 13.5 | 1
NARRABEEN | 12.2 | 0.94 | 12.3 | 0.94 | 12.5 | 0.94 | 12.7 | 0.94 | 12.8 | 0.94 | 12.6 | 0.9 | 12.5 | 0.9 | 12.5 | 0.9 | 12.6 | 0.9 | 12.9 | 0.9
NELSON BAY | 23.6 | 1 | 24.3 | 1 | 24.6 | 1 | 24.9 | 1 | 25.1 | 0.99 | 23.6 | 1 | 25 | 1 | 25.6 | 1 | 26.2 | 1 | 26.4 | 1
NEW LAMBTON | 20.4 | 0.96 | 23 | 0.96 | 23.1 | 0.96 | 23.1 | 0.96 | 23 | 0.96 | 14.5 | 0.97 | 14.4 | 0.97 | 14.4 | 0.97 | 14.4 | 0.97 | 14.5 | 0.97
NEWCASTLE CBD | 39.7 | 1 | 38.8 | 1 | 37.1 | 1 | 36.4 | 1 | 35.7 | 1 | 33.2 | 1 | 33.3 | 1 | 34 | 1 | 34.5 | 1 | 35.3 | 1
NEWPORT | 12.8 | 0.99 | 13.3 | 0.99 | 13.5 | 0.99 | 13.8 | 0.99 | 14.1 | 0.99 | 16.3 | 0.98 | 16.7 | 0.98 | 16.9 | 0.98 | 17.2 | 0.98 | 17.5 | 0.98
NORAVILLE | 27 | 0.94 | 27.9 | 0.94 | 28.5 | 0.94 | 29 | 0.94 | 29.3 | 0.94 | 24.6 | 0.98 | 25.1 | 0.98 | 25.4 | 0.98 | 25.9 | 0.98 | 26.3 | 0.98
NORTH HEAD | 17.1 | 0.92 | 17 | 0.92 | 16.9 | 0.92 | 16.8 | 0.92 | 16.7 | 0.92 | 12.3 | 0.93 | 12.2 | 0.93 | 12.2 | 0.93 | 12.1 | 0.93 | 12 | 0.93
NORTH SYDNEY | 56.2 | 0.9 | 61.5 | 0.9 | 58.7 | 0.9 | 58.1 | 0.9 | 57.2 | 0.9 | 49.7 | 0.9 | 53.5 | 0.9 | 52.1 | 0.9 | 53.4 | 0.9 | 55 | 0.9
NULKABA | 19.1 | 0.98 | 18.9 | 0.98 | 18.6 | 0.98 | 18.6 | 0.98 | 18.9 | 0.98 | 12.6 | 0.99 | 12.7 | 0.99 | 12.8 | 0.99 | 13.2 | 0.99 | 13.8 | 0.99
OLYMPIC PARK | 37.5 | 0.9 | 41.1 | 0.9 | 43 | 0.9 | 44.3 | 0.9 | 44.4 | 0.9 | 23.3 | 0.9 | 25.4 | 0.9 | 27.8 | 0.9 | 28.8 | 0.9 | 29.4 | 0.9
PADDINGTON | 30.5 | 0.99 | 30.6 | 0.99 | 30.9 | 0.99 | 31.5 | 0.99 | 32.3 | 0.99 | 30.9 | 1 | 31 | 1 | 30.9 | 1 | 31.4 | 1 | 32 | 1
PAXTON | 7.7 | 0.9 | 7.9 | 0.9 | 8 | 0.9 | 8.2 | 0.9 | 8.3 | 0.9 | 6 | 0.9 | 6.3 | 0.9 | 6.6 | 0.9 | 6.8 | 0.9 | 7 | 0.9
PEATS RIDGE | 11.4 | 0.7 | 12.1 | 0.7 | 12.2 | 0.7 | 12.5 | 0.7 | 12.7 | 0.7 | 9.8 | 0.99 | 11 | 0.99 | 11.3 | 0.99 | 11.8 | 0.99 | 12.2 | 0.99
PELICAN | 9.9 | 1 | 10.7 | 1 | 12.1 | 1 | 12.2 | 1 | 12.4 | 1 | 10.2 | 1 | 13.8 | 1 | 13.8 | 1 | 14 | 1 | 14.2 | 1
PENNANT HILLS | 80.5 | 1 | 79.8 | 1 | 79.3 | 1 | 79.6 | 1 | 80.6 | 1 | 61.3 | 0.99 | 61.4 | 0.99 | 61.3 | 0.99 | 62.2 | 0.99 | 63.6 | 0.99
PORT BOTANY | 16.6 | 0.96 | 17.3 | 0.96 | 16.6 | 0.96 | 16.4 | 0.96 | 16.3 | 0.96 | 15.6 | 0.97 | 15 | 0.97 | 14.9 | 0.97 | 14.8 | 0.97 | 14.7 | 0.97
POTTS HILL | 39.9 | 0.83 | 41.1 | 0.83 | 41.1 | 0.83 | 41.5 | 0.83 | 42 | 0.83 | 34.5 | 0.9 | 36.1 | 0.9 | 36.7 | 0.9 | 37.3 | 0.9 | 37.7 | 0.9
PUNCHBOWL | 40.2 | 1 | 40.9 | 1 | 41.1 | 1 | 41.9 | 1 | 42.9 | 1 | 37.8 | 1 | 38.7 | 1 | 39.2 | 1 | 40 | 1 | 40.7 | 1
PYMBLE | 31.8 | 0.92 | 31.9 | 0.92 | 31.9 | 0.92 | 32 | 0.92 | 32.4 | 0.92 | 30.6 | 0.98 | 31.5 | 0.98 | 31.9 | 0.98 | 32.4 | 0.98 | 32.9 | 0.98
RATHMINES | 16 | 0.99 | 16 | 0.99 | 16 | 0.99 | 16.2 | 0.99 | 16.3 | 0.99 | 11.8 | 1 | 11.7 | 1 | 11.6 | 1 | 11.7 | 1 | 11.8 | 1
RAYMOND TERRACE | 21.9 | 0.99 | 22.1 | 0.99 | 22.6 | 0.99 | 23.5 | 0.99 | 24.5 | 0.99 | 19.7 | 1 | 20.8 | 1 | 22.1 | 1 | 23.5 | 1 | 24.8 | 1
REVESBY | 46.4 | 0.94 | 46.5 | 0.94 | 46.6 | 0.94 | 46.9 | 0.94 | 47.1 | 0.94 | 41.9 | 0.98 | 42.4 | 0.98 | 42.7 | 0.98 | 43.2 | 0.98 | 43.6 | 0.98
RIVERWOOD | 28.6 | 0.95 | 29 | 0.95 | 29 | 0.95 | 29.1 | 0.95 | 29 | 0.95 | 28.8 | 0.94 | 30 | 0.94 | 30.6 | 0.94 | 31.1 | 0.94 | 31.5 | 0.94
ROCKDALE | 39.9 | 1 | 45.5 | 1 | 47.3 | 1 | 48.7 | 1 | 49.7 | 1 | 39.2 | 1 | 44.5 | 1 | 46 | 1 | 47.3 | 1 | 48.1 | 1
ROSE BAY | 39.1 | 0.9 | 41.8 | 0.9 | 42.4 | 0.9 | 43.1 | 0.9 | 43.8 | 0.9 | 45 | 0.9 | 44.8 | 0.9 | 44.5 | 0.9 | 44.9 | 0.9 | 45.3 | 0.9
ROTHBURY | 13.2 | 0.9 | 13.8 | 0.9 | 14.4 | 0.9 | 15.1 | 0.9 | 15.6 | 0.9 | 8.2 | 0.9 | 8.8 | 0.9 | 9.9 | 0.9 | 10.4 | 0.9 | 11 | 0.9
ROUCHEL | 1.3 | 0.96 | 1.3 | 0.96 | 1.3 | 0.96 | 1.3 | 0.96 | 1.4 | 0.96 | 0.9 | 0.96 | 0.9 | 0.96 | 0.9 | 0.96 | 0.9 | 0.96 | 1 | 0.96
RUTHERFORD | 33.6 | 1 | 35.1 | 1 | 35.8 | 1 | 36.4 | 1 | 37.2 | 1 | 25.2 | 1 | 26.9 | 1 | 28.2 | 1 | 29.4 | 1 | 30.5 | 1
SANS SOUCI | 17.3 | 0.98 | 17.6 | 0.98 | 17.8 | 0.98 | 18.1 | 0.98 | 18.5 | 0.98 | 16.5 | 0.99 | 16.5 | 0.99 | 16.5 | 0.99 | 16.7 | 0.99 | 17 | 0.99
SCONE | 17.9 | 1 | 17.9 | 1 | 17.9 | 1 | 18 | 1 | 18.4 | 1 | 14 | 1 | 14.2 | 1 | 14.3 | 1 | 14.5 | 1 | 15 | 1
SEFTON | 52.3 | 0.96 | 50.8 | 0.96 | 49.2 | 0.96 | 48.5 | 0.96 | 48.5 | 0.96 | 42.8 | 0.97 | 43.1 | 0.97 | 43 | 0.97 | 43.3 | 0.97 | 43.9 | 0.97
SINGLETON | 19.6 | 0.9 | 19.5 | 0.9 | 19.2 | 0.9 | 18.9 | 0.9 | 18.7 | 0.9 | 14.7 | 0.9 | 15.4 | 0.9 | 15.6 | 0.9 | 15.9 | 0.9 | 16.2 | 0.9
SINGLETON NORTH | 16.7 | 0.99 | 17.1 | 0.99 | 17.4 | 0.99 | 17.6 | 0.99 | 17.8 | 0.99 | 11.7 | 1 | 13.1 | 1 | 13.4 | 1 | 13.8 | 1 | 14 | 1
SOMERSBY | 15.5 | 0.97 | 16.5 | 0.97 | 16.9 | 0.97 | 17.2 | 0.97 | 17.6 | 0.97 | 17.9 | 0.98 | 18.9 | 0.98 | 19.5 | 0.98 | 20 | 0.98 | 20.5 | 0.98
ST IVES | 44.8 | 0.96 | 43.6 | 0.96 | 42.8 | 0.96 | 42.6 | 0.96 | 43.1 | 0.96 | 43 | 0.97 | 42.7 | 0.97 | 42.5 | 0.97 | 42.8 | 0.97 | 43.5 | 0.97
ST PETERS | 66 | 0.99 | 66.9 | 0.99 | 68.7 | 0.99 | 69.2 | 0.99 | 69.7 | 0.99 | 56.5 | 1 | 60.1 | 1 | 60.8 | 1 | 61.7 | 1 | 62.7 | 1
STOCKTON | 8.1 | 0.99 | 8 | 0.99 | 8 | 0.99 | 8 | 0.99 | 8.1 | 0.99 | 6.7 | 1 | 6.7 | 1 | 6.8 | 1 | 6.8 | 1 | 6.9 | 1
STRATHFIELD SOUTH | 30.9 | 0.99 | 31.6 | 0.99 | 31.8 | 0.99 | 32.2 | 0.99 | 32.9 | 0.99 | 25.2 | 1 | 25.7 | 1 | 25.8 | 1 | 26.1 | 1 | 26.6 | 1
SUMMER HILL | 46.6 | 0.9 | 47.3 | 0.9 | 47.6 | 0.9 | 48.1 | 0.9 | 48.9 | 0.9 | 25.8 | 0.9 | 26 | 0.9 | 25.8 | 0.9 | 26.2 | 0.9 | 26.8 | 0.9
SURRY HILLS | 27.8 | 0.9 | 45.5 | 0.94 | 45.1 | 0.94 | 44.9 | 0.94 | 45.4 | 0.93 | 24.6 | 0.9 | 41.5 | 0.95 | 41 | 0.95 | 41.4 | 0.95 | 42.5 | 0.95
SWANSEA | 12.9 | 1 | 13 | 1 | 12.9 | 1 | 12.9 | 1 | 12.9 | 1 | 12.6 | 1 | 13.1 | 1 | 13.1 | 1 | 13.3 | 1 | 13.4 | 1
TANILBA BAY | 11.3 | 0.99 | 12.2 | 0.99 | 12.6 | 0.99 | 13.3 | 0.99 | 14 | 0.99 | 10.1 | 1 | 11 | 1 | 11.4 | 1 | 12.2 | 1 | 13.1 | 1
TARRO | 20.6 | 0.96 | 20.8 | 0.96 | 21.2 | 0.96 | 21.1 | 0.96 | 21 | 0.96 | 17 | 0.96 | 18.4 | 0.96 | 18.7 | 0.96 | 19 | 0.96 | 19.2 | 0.96
TELARAH | 16.3 | 1 | 16.3 | 1 | 17 | 1 | 17.3 | 1 | 17.8 | 1 | 9.6 | 1 | 10.1 | 1 | 10.4 | 1 | 10.8 | 1 | 11.4 | 1
TERREY HILLS | 14.7 | 0.94 | 14.7 | 0.94 | 14.3 | 0.94 | 14.1 | 0.94 | 13.9 | 0.94 | 13.1 | 0.97 | 13.1 | 0.97 | 13.2 | 0.97 | 13.4 | 0.97 | 13.8 | 0.97
THORNTON | 33 | 1 | 36 | 1 | 36.3 | 1 | 36.7 | 1 | 37.2 | 1 | 18.1 | 0.99 | 19.8 | 0.99 | 20.5 | 0.99 | 21.3 | 0.98 | 22.2 | 0.98
TIGHES HILL | 21.6 | 0.97 | 22.1 | 0.97 | 22.4 | 0.97 | 22.3 | 0.97 | 22.2 | 0.97 | 24 | 0.98 | 25.5 | 0.99 | 26.2 | 0.99 | 26.9 | 0.99 | 27.4 | 0.99
TOMAGO | 13.1 | 0.95 | 14.1 | 0.95 | 14.3 | 0.95 | 14.5 | 0.95 | 14.5 | 0.95 | 14.5 | 0.96 | 15.4 | 0.96 | 16 | 0.96 | 16.4 | 0.96 | 16.6 | 0.96
TOMALPIN | 1.7 | 0.92 | 1.7 | 0.92 | 1.7 | 0.92 | 1.7 | 0.92 | 1.7 | 0.92 | 1.8 | 0.93 | 1.8 | 0.93 | 1.8 | 0.93 | 1.8 | 0.93 | 1.8 | 0.93
TOMAREE | 14.6 | 1 | 14.6 | 1 | 14.4 | 1 | 14.4 | 1 | 14.6 | 1 | 15.3 | 1 | 15.7 | 1 | 15.8 | 1 | 15.9 | 1 | 16.1 | 1
TOP RYDE | 51.5 | 0.99 | 49.9 | 0.99 | 48.7 | 0.99 | 48.1 | 0.99 | 48.1 | 0.99 | 36.5 | 1 | 35.9 | 1 | 35.8 | 1 | 36.5 | 1 | 37.8 | 1
TORONTO WEST | 20.3 | 0.99 | 20.9 | 0.99 | 21.3 | 0.99 | 21.5 | 0.99 | 21.6 | 0.99 | 15.8 | 1 | 16.7 | 1 | 17.2 | 1 | 17.6 | 1 | 17.8 | 1
TURRAMURRA | 38.5 | 1 | 37.5 | 1 | 37.1 | 1 | 37.1 | 1 | 37.6 | 1 | 36.8 | 1 | 36.8 | 1 | 36.9 | 1 | 37.3 | 1 | 37.9 | 1
UMINA | 33.2 | 0.95 | 34.1 | 0.95 | 34.2 | 0.95 | 34.6 | 0.95 | 34.7 | 0.95 | 25.6 | 0.98 | 26.3 | 0.98 | 26.3 | 0.98 | 26.7 | 0.98 | 27.2 | 0.98
VALES POINT | 6 | 0.83 | 6 | 0.83 | 6 | 0.83 | 6 | 0.83 | 6 | 0.83 | 6.3 | 0.6 | 6.3 | 0.6 | 6.3 | 0.6 | 6.3 | 0.6 | 6.3 | 0.6
WAMBERAL | 14.8 | 1 | 14.9 | 1 | 15 | 1 | 15.2 | 1 | 15.3 | 1 | 15.4 | 1 | 15.4 | 1 | 15.4 | 1 | 15.5 | 1 | 15.8 | 1
WAVERLEY | 30.3 | 0.9 | 29.8 | 0.9 | 29.6 | 0.9 | 30 | 0.9 | 30.7 | 0.9 | 40.5 | 0.9 | 39.9 | 0.9 | 39.3 | 0.9 | 39.6 | 0.9 | 40.1 | 0.9
WEST GOSFORD | 52.6 | 1 | 53.6 | 1 | 53 | 1 | 53.2 | 1 | 53.3 | 1 | 40.6 | 1 | 41.5 | 1 | 41.3 | 1 | 42.3 | 1 | 43.6 | 1
WILLIAMTOWN | 7.3 | 0.99 | 9.9 | 0.99 | 10.3 | 0.99 | 10.4 | 0.99 | 10.4 | 0.99 | 6.1 | 1 | 9.2 | 1 | 9.5 | 1 | 9.8 | 1 | 10 | 1
WOY WOY | 20.2 | 0.96 | 19.8 | 0.96 | 19.4 | 0.96 | 19.4 | 0.96 | 19.5 | 0.96 | 20 | 0.97 | 20.2 | 0.97 | 20.2 | 0.97 | 20.4 | 0.97 | 20.7 | 0.97
WYONG | 42.7 | 0.99 | 43.5 | 0.99 | 43.7 | 0.99 | 44.2 | 0.99 | 44.7 | 0.99 | 34.5 | 1 | 37 | 1 | 38.1 | 1 | 39.2 | 1 | 39.9 | 1
ZETLAND | 62.3 | 1 | 70.4 | 1 | 74.9 | 1 | 76.3 | 1 | 77.2 | 1 | 52.2 | 1 | 58.8 | 1 | 63.6 | 1 | 66.2 | 1 | 67.3 | 1
MATRAVILLE | 35.8 | 0.92 | 37.5 | 0.92 | 39 | 0.92 | 39.8 | 0.92 | 40.3 | 0.92 | 39.8 | 0.96 | 41.3 | 0.96 | 41.7 | 0.96 | 42.2 | 0.96 | 42.5 | 0.96
RNS HOSPITAL | 12.6 | 0.99 | 14.3 | 0.99 | 13.9 | 0.99 | 13.5 | 0.99 | 13.3 | 0.99 | 9.3 | 1 | 9.2 | 1 | 9.2 | 1 | 9.3 | 1 | 9.4 | 1
LEMINGTON | 2.2 | 0.96 | 2.2 | 0.96 | 2.2 | 0.96 | 2.2 | 0.96 | 2.3 | 0.96 | 1.7 | 0.97 | 1.8 | 0.97 | 1.8 | 0.97 | 1.8 | 0.97 | 1.8 | 0.97
MOUNT THORLEY | 5.4 | 1 | 5.6 | 1 | 5.7 | 1 | 5.7 | 1 | 5.8 | 1 | 4.8 | 1 | 4.9 | 1 | 5 | 1 | 5.2 | 1 | 5.4 | 1
NEWDELL | 4.8 | 0.97 | 4.9 | 0.97 | 4.9 | 0.97 | 4.9 | 0.97 | 4.9 | 0.97 | 4.4 | 0.97 | 4.4 | 0.97 | 4.4 | 0.97 | 4.4 | 0.97 | 4.4 | 0.97
GWAWLEY BAY | 28.7 | 0.99 | 27.7 | 0.99 | 27 | 0.99 | 26.9 | 0.99 | 26.9 | 0.99 | 24.8 | 0.99 | 24.6 | 0.99 | 24.5 | 0.99 | 24.6 | 0.99 | 24.9 | 0.99
LUCAS HEIGHTS | 8.4 | 0.91 | 8.4 | 0.91 | 8.4 | 0.91 | 8.4 | 0.91 | 8.4 | 0.91 | 8.1 | 0.97 | 8.2 | 0.97 | 8.3 | 0.97 | 8.3 | 0.97 | 8.3 | 0.97

## Tech Specs - (STS)
Technical Specifications - Transmission Substation
Name | Voltage Level | Area Plan | Summer | [5 empty] | Winter
|  |  | Total Capacity (MVA) | Firm Capacity (MVA) | Load Transfer Capacity (MVA) | 95% Peak Load Exceeded (hrs/yr) | Embedded Generation - Solar PV (MW) | Embedded Generation - Other (MW) | Total Capacity (MVA) | Firm Capacity (MVA) | Load Transfer Capacity (MVA) | 95% Peak Load Exceeded (hrs/yr) | Embedded Generation - Solar PV (MW) | Embedded Generation - Other (MW)
ALEXANDRIA | 132/33kV | Eastern Suburbs | 275.7 | 142.9 | 0 | 0.5 | 0 | 0 | 275.7 | 142.9 | 0 |  | 0 | 0
ARGENTON | 132/33kV | Newcastle Western Corridor | 285.8 | 142.9 | 0 | 1.5 | 44.55 | 0.51 | 285.8 | 142.9 | 0 |  | 48.07 | 0.51
AWABA | 132/33kV | Newcastle Western Corridor | 135.1 | 68.6 | 0 | 0.5 | 0.12 | 0 | 137.2 | 68.6 | 0 |  | 0.12 | 0
BANKSTOWN | 132/33kV | Canterbury Bankstown | 206.5 | 139.4 | 0 | 2.5 | 14.48 | 0 | 206.5 | 147.2 | 0 |  | 15.73 | 0
BERESFIELD | 132/33kV | Maitland | 239.8 | 150.1 | 0 | 1.8 | 46.49 | 2.1 | 239.8 | 158.6 | 0 |  | 50.17 | 2.12
BUNNERONG NORTH | 132/33kV | Eastern Suburbs | 505.1 | 312.6 | 0 | 36.5 | 17.86 | 14.66 | 505.1 | 312.6 | 0 |  | 19.82 | 14.66
CANTERBURY | 132/33kV | Canterbury Bankstown | 285.6 | 186.6 | 0 | 2 | 25.48 | 0 | 310.9 | 205.3 | 0 | 0.8 | 27.78 | 0
ERARING | 132/33kV | West Lake Macquarie | 114.3 | 57.2 | 0 | 1.3 | 8.37 | 0 | 114.3 | 57.2 | 0 |  | 9 | 0
GOSFORD | 132/33kV | Lower Central Coast | 71.4 | 0.1 | 0 | 1.5 | 63.86 | 2.06 | 71.5 | 0.1 | 0 |  | 70.24 | 2.06
HOMEBUSH | 132/33kV | Auburn/Homebush | 399.4 | 280.5 | 0 | 1.3 | 14.56 | 0 | 399.4 | 285.8 | 0 |  | 18.38 | 0
KOORAGANG | 132/33kV | Newcastle Port | 285.8 | 142.9 | 0 | 0.3 | 0.01 | 0 | 285.8 | 142.9 | 0 |  | 0.01 | 0
KURINGAI | 132/33kV | Upper North Shore | 391.3 | 260.9 | 0 | 1.8 | 63.86 | 2.06 | 411.5 | 274.4 | 0 | 5.3 | 70.24 | 2.06
KURRI | 132/33kV | Greater Cessnock | 223.4 | 156.2 | 0 | 2 | 65.45 | 0.02 | 243 | 162 | 0 |  | 69.56 | 0.02
MACQUARIE | 132/33kV | Carlingford | 284.53 | 114.32 | 0 | 13.3 | 0 | 0 | 171.47 | 114.32 | 0 | 161.3 | 0 | 0
MEREWETHER | 132/33kV | North East Lake Macquarie | 411.5 | 274.4 | 0 | 2.3 | 55.95 | 1.39 | 411.5 | 274.4 | 0 |  | 60.34 | 1.39
MITCHELL LINE | 132/66kV | Upper Hunter | 277.3 | 141.3 | 0 | 6.5 | 16.15 | 5.58 | 299.3 | 149.6 | 0 | 2.5 | 17.18 | 5.6
MUNMORAH | 132/33kV | Upper Central Coast | 156.3 | 81 | 0 | 2 | 12.35 | 0.01 | 156.3 | 81 | 0 |  | 13.31 | 0.01
MUSWELLBROOK | 132/33kV | Upper Hunter | 69.3 | 47.1 | 0 | 3 | 6.8 | 0.21 | 76.3 | 50.9 | 0 |  | 7.24 | 0.21
OURIMBAH | 132/33kV | Lower Central Coast |  |  | 0 | 5 | 26.2 | 0.01 |  |  | 0 | 2.5 | 28.09 | 0.01
PEAKHURST | 132/33kV | St George | 349.8 | 233.2 | 0 | 3 | 37.09 | 0.02 | 349.8 | 233.2 | 0 |  | 40.64 | 0.02
PORT HACKING | 132/33kV | Sutherland | 236.6 | 159.1 | 0 | 2.5 | 23.73 | 5.01 | 243 | 162 | 0 |  | 26.38 | 5.01
PYRMONT | 132/33kV | Camperdown and Blackwattle Bay | 299.1 | 170 | 0 | 8.3 | 2.04 | 0 | 299.1 | 173.5 | 0 |  | 2.18 | 0
ROZELLE | 132/33kV | Auburn/Homebush | 142.1 | 72.1 | 0 |  | 0 | 0 | 142.1 | 76.2 | 0 | 0.8 | 0 | 0
SINGLETON | 132/66kV | Singleton | 405.7 | 284.4 | 0 | 3.3 | 32.5 | 0.01 | 428.7 | 285.8 | 0 | 8.3 | 34.81 | 0.01
SURRY HILLS | 132/33kV | Eastern Suburbs | 466.4 | 346.7 | 0 | 13.3 | 4.17 | 7.97 | 466.4 | 346.7 | 0 |  | 4.31 | 7.97
SYDNEY EAST | 132/33kV | Pittwater and Terrey Hills | 233.2 | 118.1 | 0 | 2 | 29.51 | 1.04 | 233.2 | 128.8 | 0 |  | 32.73 | 1.04
TOMAGO | 132/33kV | Port Stephens | 219.3 | 153.1 | 0 | 1.5 | 59.96 | 0 | 241.3 | 161.8 | 0 |  | 64.89 | 0
WARRINGAH | 132/33kV | Manly Waringah | 273.7 | 217.4 | 0 | 2.3 | 55.41 | 2.51 | 301.1 | 229.8 | 0 | 6.5 | 61.6 | 2.51
WILLOUGHBY | 132/33kV | Lower North Shore | 338.1 | 225.4 | 0 | 4 | 12.89 | 0.1 | 349.8 | 239 | 0 | 14 | 13.86 | 0.1
GOSFORD | 132/66kV | Lower Central Coast | 349.8 | 225.4 | 0 | 2 | 0 | 0 | 349.8 | 233.2 | 0 |  | 0 | 0
OURIMBAH | 132/66kV | Lower Central Coast | 57.2 | 0 | 0 | 3 | 0 | 0 | 57.2 | 0 | 0 | 0.5 | 0 | 0
WARATAH 1 | 132/33kV | Newcastle Port | 114.32 | 57.16 | 0 | 3.5 | 0 | 0 | 114.32 | 57.16 | 0 | 90.3 | 0 | 0
WARATAH 2 | 132/33kV | Newcastle Port | 120 | 60 | 0 | 2 | 0 | 0 | 120 | 60 | 0 |  | 0 | 0
MORISSET | 132/33kV | West Lake Macquarie | 60.1 |  | 0 | 1.3 | 0 | 0 | 60.1 |  | 0 |  | 0 | 0

## Actual Demand - (STS)
Actual Demand - Transmission Substation
Name | Summer | [5 empty] | Winter
| 2020/21 (MVA) | 2020/21 (PF) | 2021/22 (MVA) | 2021/22 (PF) | 2022/23 (MVA) | 2022/23 (PF) | 2021 (MVA) | 2023 (PF) | 2022 (MVA) | 2022 (PF) | 2023 (MVA) | 2023 (PF)
ALEXANDRIA | 19.9 | 0.9 | 18.8 | 1 | 26.2 | 1 | 17.1 | 1 | 28.9 | 1 | 22.4 | 1
ARGENTON | 92.6 | 0.97 | 70.5 | 0.99 | 88.7 | 0.98 | 66.4 | 0.99 | 62.8 | 1 | 58.6 | 1
AWABA | 7.9 | 0.96 | 7.4 | 0.94 | 9.8 | 1 | 8 | 0.95 | 8.3 | 0.95 | 6.5 | 0.99
BANKSTOWN | 69 | 0.9 | 71 | 0.9 | 69.2 | 0.9 | 53.7 | 1.07 | 63 | 0.9 | 61.3 | 0.9
BERESFIELD | 87.8 | 0.96 | 90.4 | 0.96 | 94.3 | 0.97 | 71.4 | 0.99 | 67.7 | 0.99 | 66.7 | 0.99
BUNNERONG NORTH | 172.6 | 1 | 188 | 0.91 | 181.1 | 0.94 | 164.8 | 0.99 | 171.7 | 0.98 | 171.8 | 0.87
CANTERBURY | 152.7 | 0.9 | 112.6 | 0.99 | 115.6 | 0.99 | 130.5 | 1 | 110.5 | 1 | 109.5 | 1
ERARING | 16.8 | 0.98 | 15.6 | 0.98 | 17.5 | 0.99 | 16.9 | 0.98 | 15.6 | 0.95 | 15 | 0.99
GOSFORD | 24.6 | 0.98 | 26.6 | 0.97 | 22.4 | 0.98 | 20.7 | 0.98 | 25.8 | 0.99 | 18.8 | 0.99
HOMEBUSH | 74.8 | 0.99 | 93.1 | 0.99 | 99.4 | 1 | 79.2 | 1 | 76.6 | 1 | 76.1 | 1
KOORAGANG | 64.2 | 0.93 | 63 | 0.92 | 68.7 | 0.93 | 68.6 | 0.96 | 66.2 | 0.93 | 63.6 | 0.95
KURINGAI | 155.5 | 0.9 | 137.3 | 0.9 | 140.1 | 0.9 | 145.9 | 0.99 | 144.1 | 0.9 | 141.9 | 0.9
KURRI | 130.2 | 0.95 | 106.8 | 0.97 | 116.9 | 0.98 | 92.7 | 0.97 | 86.1 | 0.97 | 93.9 | 0.99
MACQUARIE |  |  |  |  | 26.4 | 0.98 | 22.9 | 0.9 |  |  | 26.6 | 0.99
MEREWETHER | 166.1 | 0.96 | 138.2 | 0.97 | 158.4 | 0.9 | 141.5 | 0.98 | 132 | 0.9 | 123.1 | 0.9
MITCHELL LINE | 70.3 | 0.96 | 64.3 | 0.96 | 70.1 | 0.97 | 69.9 | 0.96 | 69.4 | 0.9 | 70.3 | 0.96
MUNMORAH | 31.9 | 0.94 | 24.9 | 0.96 | 28.7 | 0.97 | 31.3 | 0.94 | 28.5 | 0.96 | 26 | 0.99
MUSWELLBROOK | 21.2 | 0.97 | 14.8 | 0.97 | 15.7 | 0.98 | 15.4 | 0.98 | 13.9 | 0.99 | 13.8 | 0.99
OURIMBAH | 13.6 | 0.93 | 12.3 | 0.97 | 11.8 | 0.94 | 12 | 0.99 | 11.2 | 0.97 | 11.4 | 0.96
PEAKHURST | 108.8 | 0.99 | 106.7 | 1 | 112.1 | 1 | 111.3 | 0.99 | 108.3 | 0.95 | 97.9 | 1
PORT HACKING | 95.8 | 0.9 | 87.9 | 0.99 | 93.2 | 0.99 | 82.7 | 1 | 85.6 | 1 | 96.7 | 0.9
PYRMONT | 92 | 0.9 | 66.8 | 0.9 | 71.3 | 0.9 | 71.1 | 0.97 | 59.4 | 0.9 | 58.5 | 0.9
ROZELLE | 12.2 | 0.9 | 12 | 0.66 | 10.5 | 0.9 | 10.3 | 0.9 | 12 | 0.67 | 14.1 | 0.9
SINGLETON | 147.6 | 0.93 | 130.1 | 0.99 | 137.3 | 0.94 | 133.9 | 1 | 136.9 | 0.95 | 136.1 | 0.9
SURRY HILLS | 136.3 | 1 | 138.5 | 1 | 134.6 | 0.99 | 134.4 | 0.98 | 122.5 | 1 | 123.4 | 0.9
SYDNEY EAST | 81 | 0.99 | 65.9 | 0.95 | 74.9 | 0.94 | 75.2 | 0.99 | 70.6 | 0.98 | 66.4 | 1
TOMAGO | 125.8 | 0.96 | 103.4 | 0.98 | 115.7 | 0.98 | 108.3 | 0.96 | 96.2 | 0.99 | 95.6 | 0.99
WARRINGAH | 164.7 | 1 | 176.4 | 1 | 161.3 | 1 | 188.8 | 0.99 | 204.4 | 1 | 162.5 | 1
WILLOUGHBY | 105.3 | 0.98 | 102.6 | 1 | 94.8 | 1 | 103.1 | 0.97 | 104 | 0.97 | 95.5 | 1
GOSFORD | 139.2 | 1 | 122.9 | 0.98 | 127 | 0.99 | 126.8 | 0.99 | 113.8 | 1 | 107.8 | 1
OURIMBAH | 48.6 | 0.97 | 42.2 | 0.99 | 48.9 | 0.99 | 52.5 | 0.99 | 48.4 | 0.99 | 46.3 | 1
WARATAH 1 | 46.2 | 0.9 | 46.4 | 0.9 | 35.7 | 0.9 | 47 | 0.9 | 48.3 | 0.9 | 36.5 | 0.9
WARATAH 2 | 21.4 | 0.86 | 28.9 | 0.86 | 27.7 | 0.88 | 33.1 | 0.89 | 20.8 | 0.9 | 14.7 | 0.89
MORISSET | 16 | 0.87 | 14.3 | 0.91 | 20.1 | 0.85 | 15 | 0.92 | 18.6 | 0.81 | 13 | 0.88

## Demand Forecast - (STS)
Demand Forecast - Transmission Substation
Name | Summer | [9 empty] | Winter
| 2023/24 (MVA) | 2023/24 (PF) | 2024/25 (MVA) | 2024/25 (PF) | 2025/26 (MVA) | 2025/26 (PF) | 2026/27 (MVA) | 2026/27 (PF) | 2027/28 (MVA) | 2027/28 (PF) | 2024 (MVA) | 2024 (PF) | 2025 (MVA) | 2025 (PF) | 2026 (MVA) | 2026 (PF) | 2027 (MVA) | 2027 (PF) | 2028 (MVA) | 2028 (PF)
ALEXANDRIA | 42.5 | 1 | 46.2 | 1 | 61.7 | 1 | 106.7 | 1 | 148 | 1 | 45.2 | 1 | 49.5 | 1 | 65.2 | 1 | 110.7 | 1 | 152.7 | 1
ARGENTON | 100.5 | 0.98 | 99.5 | 0.98 | 98.5 | 0.98 | 98.3 | 0.98 | 98.7 | 0.98 | 62.8 | 1 | 63.6 | 1 | 63.8 | 1 | 64.6 | 1 | 65.5 | 1
AWABA | 8.9 | 1 | 8.9 | 1 | 8.9 | 1 | 8.9 | 1 | 8.9 | 1 | 7.6 | 0.99 | 7.6 | 0.99 | 7.6 | 0.99 | 7.6 | 0.99 | 7.6 | 0.99
BANKSTOWN | 69.8 | 0.99 | 70.2 | 0.99 | 70.2 | 0.99 | 70.9 | 0.99 | 71.8 | 0.99 | 58.1 | 1 | 59.3 | 1 | 60 | 1 | 60.9 | 1 | 61.7 | 1
BERESFIELD | 101.6 | 0.97 | 104.6 | 0.97 | 104.3 | 0.97 | 105.4 | 0.97 | 106.6 | 0.97 | 74 | 0.99 | 77.5 | 0.99 | 79.7 | 0.99 | 82 | 0.99 | 84.1 | 0.99
BUNNERONG NORTH | 182.4 | 0.97 | 185.6 | 0.96 | 191.4 | 0.96 | 192.5 | 0.96 | 193.3 | 0.96 | 170 | 0.95 | 177.1 | 0.95 | 179.5 | 0.94 | 181.7 | 0.94 | 184.2 | 0.94
CANTERBURY | 140.6 | 0.99 | 140.3 | 0.99 | 141.2 | 0.99 | 149.5 | 0.99 | 150.8 | 0.99 | 126.4 | 1 | 126.7 | 1 | 127.7 | 1 | 136.2 | 1 | 137.7 | 1
ERARING | 19.4 | 0.99 | 20 | 0.99 | 21.7 | 0.99 | 22.2 | 0.99 | 22.8 | 0.99 | 16.6 | 0.99 | 19.8 | 0.99 | 20.3 | 0.99 | 20.9 | 0.99 | 21.6 | 0.99
GOSFORD | 27 | 0.98 | 27 | 0.98 | 27.8 | 0.98 | 28 | 0.98 | 28.3 | 0.98 | 20.8 | 0.99 | 20.8 | 0.99 | 21.4 | 0.99 | 21.6 | 0.99 | 21.9 | 0.99
HOMEBUSH | 56.5 | 1 | 57.5 | 1 | 68.8 | 1 | 68.5 | 1 | 68.6 | 1 | 69.7 | 1 | 74.8 | 1 | 88.9 | 1 | 90.9 | 1 | 92.1 | 1
KOORAGANG | 67.1 | 0.93 | 74.6 | 0.93 | 78.7 | 0.93 | 78.7 | 0.93 | 81.2 | 0.93 | 67.2 | 0.96 | 74.8 | 0.96 | 74.8 | 0.96 | 78.9 | 0.96 | 81.4 | 0.96
KURINGAI | 152.3 | 0.9 | 150.1 | 0.9 | 148.5 | 0.9 | 148.6 | 0.9 | 150.1 | 0.9 | 147.8 | 0.9 | 148.1 | 0.9 | 148.2 | 0.9 | 149.6 | 0.9 | 151.8 | 0.9
KURRI | 136.8 | 0.98 | 136.9 | 0.98 | 139.5 | 0.98 | 141.5 | 0.98 | 144.2 | 0.98 | 92.3 | 0.99 | 96.4 | 0.99 | 99.3 | 0.99 | 102.8 | 0.99 | 106.6 | 0.99
MACQUARIE | 36.4 | 0.98 | 66.6 | 0.98 | 96 | 0.98 | 148.4 | 0.98 | 200.5 | 0.98 | 50.7 | 0.99 | 64.5 | 0.99 | 88.9 | 0.99 | 141 | 0.99 | 190.5 | 0.99
MEREWETHER | 141.1 | 0.98 | 142.9 | 0.98 | 141.9 | 0.98 | 140.9 | 0.98 | 140.7 | 0.98 | 123.7 | 0.98 | 129.2 | 0.98 | 130.9 | 0.98 | 133 | 0.98 | 135.2 | 0.98
MITCHELL LINE | 79.5 | 0.97 | 80.5 | 0.97 | 80.9 | 0.97 | 81.8 | 0.97 | 82.9 | 0.97 | 75.3 | 0.96 | 76.6 | 0.96 | 77.2 | 0.96 | 78.2 | 0.96 | 79.4 | 0.96
MUNMORAH | 30.1 | 0.97 | 31 | 0.97 | 31.7 | 0.97 | 32.2 | 0.97 | 32.4 | 0.97 | 28.6 | 0.99 | 29.1 | 0.99 | 29.5 | 0.99 | 29.9 | 0.99 | 30.3 | 0.99
MUSWELLBROOK | 23.1 | 0.99 | 24.1 | 0.99 | 24.6 | 0.99 | 24.8 | 0.99 | 24.9 | 0.99 | 14.5 | 0.99 | 15.3 | 0.99 | 15.6 | 0.99 | 15.8 | 0.99 | 15.9 | 0.99
OURIMBAH | 13.6 | 0.94 | 14.3 | 0.94 | 14.3 | 0.94 | 14.6 | 0.94 | 14.8 | 0.94 | 11.9 | 0.96 | 13 | 0.96 | 13.3 | 0.96 | 13.8 | 0.96 | 14.2 | 0.96
PEAKHURST | 116.4 | 1 | 118 | 1 | 118.7 | 1 | 119.6 | 1 | 120.3 | 1 | 109 | 1 | 110.8 | 1 | 111.6 | 1 | 113.6 | 1 | 115.4 | 1
PORT HACKING | 89.1 | 0.99 | 90.2 | 0.99 | 89.5 | 0.99 | 89.4 | 0.99 | 89.2 | 0.99 | 98.7 | 0.9 | 99.9 | 0.9 | 100.5 | 0.9 | 101.6 | 0.9 | 102.5 | 0.9
PYRMONT | 67.3 | 0.99 | 95.1 | 0.98 | 100.2 | 0.97 | 103.4 | 1 | 107.8 | 1 | 64 | 1 | 79.8 | 0.99 | 88.5 | 0.98 | 94 | 0.98 | 99.5 | 0.98
ROZELLE | 16.1 | 0.89 | 23.6 | 0.9 | 43.6 | 0.9 | 43.6 | 0.9 | 43.6 | 0.9 | 24.6 | 0.89 | 35 | 0.89 | 44.4 | 0.89 | 44.4 | 0.89 | 44.4 | 0.89
SINGLETON | 146.6 | 0.99 | 166.2 | 0.99 | 171.8 | 0.99 | 172.1 | 0.99 | 172.6 | 0.99 | 126.6 | 0.98 | 128.5 | 0.98 | 148.7 | 0.97 | 149.7 | 0.97 | 150.7 | 0.97
SURRY HILLS | 148.3 | 1 | 164.4 | 1 | 163.5 | 1 | 163.4 | 1 | 164.9 | 1 | 122 | 1 | 135.8 | 0.99 | 135.2 | 0.99 | 136.2 | 0.99 | 138.6 | 0.99
SYDNEY EAST | 76.7 | 0.94 | 77.5 | 0.94 | 77.4 | 0.94 | 77.9 | 0.94 | 78.6 | 0.94 | 70.5 | 1 | 70.7 | 1 | 70.6 | 1 | 71.5 | 1 | 72.7 | 1
TOMAGO | 127.5 | 1 | 133.2 | 1 | 134.9 | 1 | 137.5 | 1 | 140.2 | 1 | 105.3 | 1 | 112.6 | 1 | 116 | 1 | 119.8 | 1 | 123 | 1
WARRINGAH | 165.5 | 1 | 167.9 | 1 | 168.4 | 1 | 169.5 | 1 | 170.9 | 1 | 180.8 | 1 | 181.7 | 1 | 182.1 | 1 | 184.6 | 1 | 187.8 | 1
WILLOUGHBY | 123.5 | 1 | 129.7 | 1 | 148.6 | 0.99 | 167.9 | 0.99 | 178.5 | 0.99 | 126.7 | 1 | 134.9 | 1 | 151.5 | 1 | 170.7 | 0.99 | 183.4 | 0.99
GOSFORD | 142.2 | 1 | 142.7 | 1 | 142 | 1 | 142.5 | 1 | 142.9 | 1 | 113.6 | 1 | 114.4 | 1 | 114.1 | 1 | 115.5 | 1 | 117.4 | 1
OURIMBAH | 53.8 | 0.99 | 55.2 | 0.99 | 55.8 | 0.99 | 56.4 | 0.99 | 56.7 | 0.99 | 48.3 | 1 | 48.9 | 1 | 48.7 | 1 | 49.1 | 1 | 49.7 | 1
WARATAH 1 | 34.5 | 0.89 | 34.5 | 0.89 | 34.5 | 0.89 | 34.5 | 0.89 | 34.5 | 0.89 | 39.6 | 0.92 | 39.6 | 0.92 | 39.6 | 0.92 | 39.6 | 0.92 | 39.6 | 0.92
WARATAH 2 | 32.1 | 0.91 | 32.1 | 0.91 | 32.1 | 0.91 | 32.1 | 0.91 | 32.1 | 0.91 | 19.5 | 0.94 | 19.5 | 0.94 | 19.5 | 0.94 | 19.5 | 0.94 | 19.5 | 0.94
MORISSET | 22.4 | 0.85 | 24 | 0.85 | 24 | 0.85 | 24 | 0.85 | 24 | 0.85 | 16.2 | 0.9 | 16.2 | 0.9 | 16.2 | 0.9 | 16.2 | 0.9 | 16.2 | 0.9